KTH Industrial Engineering and Management

Investigation of Thermal Biomass Gasification for Sustainable Small Scale Rural Electricity Generation in Uganda

Joseph Olwa

Licentiate Thesis 2011

Division of Energy and Climate Studies Department of Energy Technology KTH School of Industrial Engineering and Management STOCKHOLM, SWEDEN

ISBN 978-91-7501-045-8 ISRN KTH/KRV /11/06-SE ISSN 1100-7990 TRITA KRV Report 11/06 © Joseph Olwa

Abstract

With the increasing need for renewable energy technologies in the world, biomass fuel transformation technology is growing towards meeting that need, among others. Challenges remain certain and new innovations are being tested in bid to overcome them with the application of biomass as energy source. This report presents some studies carried out into understanding the potential and challenges associated with utilization of biomass fuel, especially for technologies that are appropriate for rural applications. Utilization of biomass gasification technologies is in the focus of this study.

The great potential biomass fuel provide to Uganda for possible energy production in small scale application is presented. This study was carried out to understand the possibility of using biomass as fuel in electricity power generation in Uganda. It takes into consideration the use of biomass gasification technology in energy production. Challenges related to the application of biomass fuels are discussed, mostly with tar and alkali metal compounds in the gas stream.

Suggested methods to combat some of the challenges with biomass fuels are pointed out in this study. Application of externally fired gas turbine (EFGT) system is a particular approach discussed and its technical performance analyzed. The analysis revealed that efficiency of the EFGT system is greatly dependent on the heat exchanger effectiveness and on turbine inlet temperature. Optimum performance can be realized with air compression ratio of 3.4. It is also noted that fouling and deposition in the heat exchanger can affect its performance.

A related study carried out was on the retention of alkali metals in an updraft gasifier. The gasifier was chosen for possible integration with the EFGT system. Finding was that about 99% of the alkali metals are retained in the gasifier. It is anticipated that this would reduce on the deposition in the heat exchanger, reducing on maintenance time. A need is identified to determine the level of deposition mentioned. A simple thermodynamic modeling of the alkali metals condensation reaction on a high temperature heat exchanger surface was conducted. The results showed that with appropriate quantity of S in the raw fuel, alkali metals bounding with Cl are greatly reduced. Cl is passed out as gaseous HCl, leaving deposition of none corrosive sulphates. Recommendation is made to study this phenomenon in an experimental setting.

Biomass gasification technology integration with an internal combustion (IC) engine is also studied. Here requirements for the producer gas quality have been discussed. Some tests carried out with wood pellets and wood cylinders compared the yield of tar from the two physically different fuels. Wood pellets were found to yield more tar than wood cylinders.

Economic analysis of biomass gasifier integrated with an IC engine running a generator of 100 kWe was carried out. Comparison with a diesel electricity generator of similar capacity was made for a scenario in Uganda over a project life of 20 years. Different Plant Capacity Factors (PCF) and fuel costs including subsidies were considered. The analysis showed that over long period of time biomass power plant was more beneficial than the diesel power plant at PCF over 40%. This is more pronounced with unsubsidized diesel fuel.

Acknowledgement

I thank God for His awesome grace in letting me see this work to its completion.

The research was sponsored by the Swedish International Development Agency, SIDA, through its capacity building program for Makerere University, Kampala. I am very grateful for the funding without which it would have been very difficult.

I would like to express my deepest gratitude to the Head of Energy Department at KTH, Prof. Torsten Fransson, for the supervision and support he provided during my efforts to accomplish this work. Many thanks also go to staffs and colleagues of the Energy Department of KTH who worked with me in the various aspects of this study. I am also indebted to Prof. em Bjorn Kjellstrom from Lulea Technical University and Prof. Mackay Okure from the College of Engineering Design and Art of Makerere University for their supervision and moral support which they provided during the course of this study.

My sincerely appreciation also is extended to Prof. Marcus Ohman of the Energy Department of Lulea Technical University through whom some of the experiments were made possible.

I would also like to thank my dear wife and daughter, Susan and Hebron, for their patience and encouragement which created a beautiful atmosphere for my work.

Joseph Olwa

Stockholm 2011

Abbreviations

| Mg | micrograms |
| --- | --- |
| ASME | American Society of Mechanical Engineers |
| ASTM | American Society of Testing and Materials |
| CHP | Combine heat and power |
| EFGT | externally fired gas turbine |
| FAO | Food Agricultural Organization |
| GDP | Gross Domestic Product |
| GJ | giga-joule |
| GT | gas turbine |
| GW | giga-watt |
| GWh | giga-watt-hour |
| hp-h | horse power-hour |
| IC | internal combustion |
| ICP-AES | Inductively coupled plasma atomic emission spectroscopy |
| IRR | internal rate of return |
| KCC | Kampala City Council |
| kg | kilogram |
| kJ | kilo-joule |
| kW | kilo-watt |
| kWe | kilo-watt-electric |
| kWh | kilo-watt-hour |
| kWt | kilo-watt-thermal |
| L | liters |
| Max. | maximum |
| Min. | minimum |
| MJ | mega-joule |
| MS | Mass Spectroscopy |
| MSW | municipal solid waste |
| MWe | mega-watt-electric |
| MWh | mega-watt-hour |
| MWt | mega-watt-thermal |
| Nm3 | normal cubic meter |
| NPV | net present value |
| O&M | Operation and Maintenance |
| OLGA | Dutch acronym for oil-based gas washers |
| OPEC | Organization of Petroleum Exporting Countries |
| PBP | payback period |
| ppbw | part per billion weight |
| PPP | purchase powerparity |

| SPA | solid phase absorption |
| --- | --- |
| TARWATC | tar-water treatment and condensation |
| TEMA | Tubular Exchangers and Manufacturers Association |
| TIT | turbine inlet temperature |
| TWh | tera-watt-hour |
| UNS | Universal Number System |
| WBG | Wood Based Gasifier |
| wt | weight |
| VTT | Finnish acronym for governmental technical research center |
| XRD | X-ray diffraction |

Nomenclature

The symbols used in equations in the text are explained immediately below the equation where the symbols appear.

TABLE OF CONTENT

Abstract	iii

Acknowledgement	iv

Abbreviations	v

Nomenclature	vi

Index of Tables	xii

- INTRODUCTION	13

  - Background	13

  - Objective of the study	15

    - General objective	15

    - Specific objectives	16

  - Conceptual Framework	16

  - Overview of the Contents of the Thesis	18

- DEVELOPMENTS IN BIOMASS GASIFICATION TECHNOLOGY	19

  - A Brief Background	19

  - Thermal Gasification of Biomass	19

2.2.1 Gasification process	20

  - Gasifier types	21

    - Downdraft gasifiers	21

    - Updraft gasifiers	23

    - Fluidized bed gasifiers	23

    - Entrained flow gasifier	24

    - Some Aspects on Applications of Gasifiers	25

  - Contaminants in the Producer Gas	26

    - Tar in producer gas	26

    - Tar treatment methods in selected biomass gasification technologies	28

    - Alkali metals in producer gas	32

    - Particles in producer gas	33

  - Producer Gas Applications	33

    - Gas quality requirements	33

    - Cooled gas for IC engines applications	35

    - Hot gas for turbine application	37

  - Conclusions and Recommendations	39

- DESIGN CONSIDERATIONS FOR AN EXTERNALLY FIRED MICRO GAS TURBINE (EFGT) HEAT EXCHANGER USING BIOMASS AS FUEL	41

3.1 Introduction	41

- EFGT System Modeling and Simulation	41

3.2.1 Method and assumptions	41

- Results and Discussion on EFGT Technical Performance	42

- Heat Exchanger Design Considerations	43

- Consideration of Uncertainty in the Heat Exchanger Design	44

- Simulation to Determine Heat Exchanger Design Uncertainties	46

- Monte Carlo simulation	46

- Application of Monte Carlo	47

- Determination of number of iterations	48

  - Discussion on Uncertainty Analysis Results	48

  - Conclusions and Recommendation	50

    - ALKALI METAL COMPOUNDS RETENTION IN AN UPDRAFT GASIFIER	51

      - Introduction	51

      - Experiments	52

        - Equipment description	52

        - Experimental method	53

        - Measurement technique and sampling methods	54

      - Results and Discussion	55

        - Ultimate analysis	55

        - Temperature profiles	55

        - Gas composition	59

        - Particulates analysis	60

        - Alkali metals distributions	63

      - Thermo-Chemical Modeling of Alkali Metal Compounds Condensation Reaction in Higher Temperature Heat Exchanger	67

4.4.1 Alkali compounds condensation reactions	67

      - Conclusions and Recommendation	69

    - DOWNDRAFT GASIFIER PRODUCT GAS TAR CONTENT FROM WOOD PELLETS AND WOOD CYLINDERS FUELS	71

      - Introduction	71

      - Experiment	72

        - Fuel	72

        - Experimental setup	72

        - Procedure	74

      - Results	75

      - Discussion	76

      - Conclusions	78

    - EFFECTS OF TAR SAMPLE STORAGE ON ANALYSIS RESULTS	79

      - Introduction	79

      - Experimental Setup and procedure	80

      - Analysis Results and Discussion	80

      - Statistical Treatment of Results	82

      - Conclusion and Recommendations	83

    - FIELD STUDY OF A BIOMASS GASIFIER IC ENGINE SYSTEM	84

      - Introduction	84

      - Description of the installation	84

      - Operational Experiences	86

      - Possible Reasons for the Degradation of the Output	87

        - Low density of the fuel-air mixture entering the cylinder	87

        - Poor heating value of the fuel-air mixture	87

        - Low conversion efficiency of the engine	87

      - Evaluation of the fuel gas preparation process	88

        - Wood moisture content	88

        - Wood consumption	88

        - Gasifier performance	89

        - Pressure drop across the gas filters	92

        - Conversion efficiencies	93

      - Tests on the gas engine	94

        - Check on compression ratio for the IC engine	94

        - Exhaust gas analysis	96

      - Discussion	97

      - Conclusions and Recommendations	98

    - BIOMASS GASIFICATION INVESTMENT OPPORTUNITY FOR SMALL SCALE APPLICATIONS IN UGANDA	99

      - Introduction	99

      - Biomass Fuels - Availability Issues	100

      - Biomass Gasifier and Diesel systems	101

      - Economics of Biomass and Diesel Systems	102

      - Issues with Biomass Gasification Technology Systems in Uganda	105

      - Conclusions	106

    - FUTURE WORK	107

REFERENCES	109

Index of Figures

Figure 1: Conceptual frame work outline	17

Figure 2: Conversion of biomass into producer gas.	Source:

http://www.members.tripod.com/~cturare/pro.htm	20

Figure 3: Downdraft gasifier	22

Figure 4: Updraft gasifier. Source: http://www.knowledgepublications.com	23

Figure 5: Fluidized bed gasifier. Source: FAO1181	24

Figure 6: Entrained bed gasifier. Source: www.netl.doe.gov/.../gasification/basics/4.html	24

Figure 7: Two stage gasification process[32]	28

Figure 8: OLGA gas cleaning process [34]	29

Figure 9: Carbona Gasifier and gas cleaning technology[36]	30

Figure 10: Process for purification of tar condensate under Babcock & Wilcox Volund[37]	31

Figure 11: Dual power gasifier for the production of low tar and high tar content producer gas installed at

Entimos Oy, Finland1381	32

Figure 12: Biomass-gasifier IC engine system	36

Figure 13: Directly fired GT scheme	38

Figure 14: EFGT system Scheme	38

Figure 15: (a) Variation of system efficiency with pressure ratios at different TIT and (b) Vartiation of Net power

output with presure ratio for different TIT.	43

Figure 16: Normal distribution curve	49

Figure 17: Monte Carlo Simulation used to determine design factor for the heat exchanger surface area	49

Figure 18: Photograph of grate viewed from underside with the ash pot removed after first wood pellets

gasification	52

Figure 19: Gasifier details: (a) construction dimensions in mm, (b) Connections of components, and (c)

motorized half-closed ball valve model	53

Figure 20: Temperature time plot at different heights (z) along the gasifier central axis for first wood pellets

experiment 1	56

Figure 21: Temperature time plot at different heights (z) near the gasifier wall for first wood pellets experiment

1	57

Figure 22: Time temperature profile at different heights (z) along gasifier central axis for wood pellets

experiment 2	57

Figure 23: Temperature -time plot at different heights (z) along the gasifier central axis for first reed canary

grass experiment	58

Figure 24: Temperature -time plot at different heights (z) near the wall in the fuel bed for first reed canary grass

experiment	58

Figure 25: Gas composition from wood pellets experiment	59

Figure 26: Gas composition from wood pellets experiment 2	59

Figure 27: Gas composition from reed canary grass gasification experiment 1	60

Figure 28: Photograph of thermocouple tubes showing parts of the normal and the melted tubes including

thermocouple wires during the reed canary grass pellets gasification	61

Figure 29: Condensed tar after the filter in half of the filter housing (b) Filter holder simplified drawing	62

Figure 30: Distribution of ingoing K (a) and Na (b) in the producer gas and the different solid residues fractions

during the second experiment with wood pellets	65

Figure 31: Distribution of ingoing K (a) and Na (b) in the producer gas and the different solid residues fractions

during the second experiment with wood pellets	65

Figure 32:Chemical equilibrium diagram for cooling of the flue gases(produced by combustion of the wood

pellet based producer gas in air to fuel ratio of 1.1) from 1100-400 C for the K-system	68

Figure 33: Chemical equilibrium diagram for cooling of the flue gases (produced by combustion of the wood

pellets based producer gas in an air fuel ratio of 1.1) from 1100-400 C for the S system	68

Figure 34: Chemical equilibrium diagram for cooling of the flue gases (produced by combustion of the wood

pellet based producer gas in an air to fuel ration of 1.1) from 1100-400C for the Cl- system	69

Figure 35: Gasifier system setup	73

Figure 36 : Diagram Showing a Cut Section through the down draft and Section B-B showing the combustion

zone details 	 73

Figure 37: Sampling unit[76]	74

Figure 38: Combustion zone temperature with wood pellets and wood cylinders	75

Figure 39: Reduction zone temperature with wood pellets and wood cylinders	75

Figure 40: Plot of ultimate analysis tests on wood char from wood cylinders and pellets	76

Figure 41: Tar group sample quantities	80

Figure 42: Flow scheme for the Muzizi power plant	85

Figure 43: Specific fuel consumption determined from logbook data and measured on two site visits	89

Figure 44: Power output and specific wood consumption in the Muzizi power plant in year 2009 and 2010	89

Figure 45: Three photographs showing combustion process as viewed through the nozzle hole	91

Figure 46: Char samples from Muzizi power plant	91

Figure 47: Compression machine operation	94

Figure 48: Compression Test Results	95

Figure 49: Turbo charger unit scheme and gas flow	96

Figure 50: Muzizi exhaust emission 1900-2000hrs	97

Figure 51: Electricity costs estimates at different PCF with biomass and subsidized diesel prize 0.203 $/kWh. 103 Figure 52: Electricity Costs Estimates at different PCF with biomass and unsubsidized diesel price of 0.28 $/kWh

103

Figure 53: Electricity costs estimates at different PCF with biomass and a subsidized diesel price US$

0.1015/kWh	104

Figure 54: Costs percentage contribution for (a) diesel system with fuel cost at US$0.280/kWh and (b) biomass system with fuel cost at US$0.03/kWh	104

Index of Tables

Table 1: Fuel potential of some agricultural residues in Uganda	14

Table 2: Producer gas composition from Wood and Charcoal gasification in downdraft gasifier	22

Table 3: Characteristics of different gasification configurations (source. www.bgtworld.com)	25

Table 4: Advantages and challenges of gasifying agents, gasifier design and gasifier operations [22]	26

Table 5: VTT Demonstration plant	30

Table 6: Gas quality requirements for gas turbines and IC engines[27] [47]	35

Table 7: Different gasifier Tar and particulates loads[47]	35

Table 8: Heat Exchanger Specification Sheet	45

Table 9: Some of the maximum and minimum values of parameters used in Monte Carlo Simulation	47

Table 10: Raw fuel composition including main ash-forming elements of the used pellet fuels	55

Table 11: K and Cl-content (re-calculated to concentrations in producer gas) in solid material trapped in the total particle filter ash during the initial experiments with wood and reed canary grass pellets,

respectively	62

Table 12: K, Na, Pb, V, S, Cl, Ca and Mg content (re-calculated to concentrations in producer gas) in solid material trapped in the total particle filter ash and in the gas wash bottles during the second

experiment with wood pellets	63

Table 13: Acceptable contaminant concentration in fuel for LM2500 gas turbine. Source : Nelson[65]	63

Table 14: Elemental composition (main ash forming elements and some interesting trace elements) of the

different solid residue samples produced in the second experiment with wood pellets	64

Table 15: Phase identified (wt% of crystalline phase)* in the different solid residue samples produced in the

second experiment with wood pellets	64

Table 16: Fuel consumption and residues obtained from the experiments	66

Table 17: Elements and solution models used in the chemical equilibrium model calculations [73]	67

Table 18: Wood fuels analysis results	72

Table 19: Average tar composition in g/Nm3 of gas	77

Table 20: Quantities of Tar constituents in x102g/Nm3 of Producer gas an updraft gasifier	81

Table 21: Group statistics with quantities in mg/Nm3	82

Table 22: Testing differences between sample means	82

Table 23: Correction Factors for Tar Storage	83

Table 24: Results of moisture content for Muzizi Plant	88

Table 25: Gasifier mass balance at 46 kWe	92

Table 26: Pressure drop across the gas filters	93

Table 27: Gasifier energy balance at 46kWe	93

Table 28: Pressure readings from Muzizi power plant gas engine	96

Table 29: Uganda electricity tariff by consumer category	100

Table 30: The variation of heating value with different oxidizers for biomass fuel	101

1. Introduction

1.1 Background

Uganda's energy consumption per capita is very low at only 3923 kWh (337kg oil Equivalent) [1]compared to United States of America at 91702 kWh (7886kg oil Equivalent) [2]recorded in 2007. The main energy supply, in Uganda, is derived from biomass sources at 92.1%, followed by petroleum products 6.9%, leaving electricity at only 1%. The recorded national electricity access in 2007 was about 9% and is a very low figure when compared to a developed country like Singapore 100% and to a developing country like Egypt with 80% [3].

Most urban areas of Uganda where extension of power grids cannot be economically viable are utilizing diesel powered electricity generators. Most of these generators are state owned while others are owned by private entrepreneurs. Such installations are meeting domestic and small commercial electricity needs in grid isolated areas. Some of these areas have resources, which encouraged small scale industrial growth. The high cost on imported fossil fuels in Uganda has repressed its application in power generation for addressing the electricity need, yet electricity is considered one of the vital components in enhancing economic and social development. Thus, the unmet electricity demand has belated developments in most rural areas of Uganda.

There are other renewable energy options to consider when it comes to electricity power generation in Uganda with the choices limited by; lack of investment capital, unsecured investment environment and lack of technical knowhow, among others. These options are; geothermal, Wind, Solar and Hydro power resources. When biomass is compared to aforementioned resources, it still offers an affordable alternative in the generation of electricity power, especially in small scale applications for rural and isolated settlements. The availability of biomass resources and its wide spread consumption in Uganda; present a potential platform to transform it in to a sustainable, efficient, and effective energy source.

The possible energy sources for electricity generation from biomass in Uganda are; wood and its products/residues, agricultural/farmland residues and MSW. MSW generation is attractive with the increasing population in urban areas generating more wastes. According to Kampala City Council (KCC), 1500 tons/day of wastes are generated in the city of Kampala, Uganda [4]. The waste collection rate is about 45% which leaves 55% unaccounted for due to lack of equipment and personnel to manage the collection. Similar trends can be speculated for the other bigger towns in Uganda like Mbale and Mbarara. MSW can be a sturdy source for electricity power production through gasification, especially with its 80% organic matter content which is

combustible [5].

Estimation of the wood biomass potential stands at about 27.7 million tons of accessible and sustainable supply, which is equivalent to 140TWh of energy. The accessibility refers to ease of harvesting and transportation to consumption points, which in most cases come at considerable costs. Planned energy plantations are one possibility for making these resources more economically viable and sustainable. It is sometimes argued that electrification opens possibilities for reduced use of wood fuel for domestic use and commercial activities such as in ceramic industries. A study done in Uganda concluded, however, that this is not realistic within the forecasting horizon due to the high electricity tariff [6]. Unless new ways are identified and explored to allow sustainable utilization of wood fuel, their consumption as the main energy resource put a very unsustainable demand on the forest wood. This if not controlled will cause adverse environmental degradations in a few years to come [7]. Through proper planning and implementation of policies on sustainable utilization of woody biomass, and with supplement from agricultural residues and MSW, it is possible to avert detrimental effects to the environment that can occur through traditional methods of wood fuel consumption.

Residues from processing of agricultural products represent a cheap source for bioenergy. Two such residues available in large quantities in Uganda are coffee husk and bagasse. Large amounts are being used as fuel but there are significant amounts that are not utilized as shown in Table 1, based on a 2004 estimate [5].

Table 1 : Fuel potential of some agricultural residues in Uganda

| Fuel | Production (Metric tons) | Exces s /unutilized (Metric tons) | Estimated energy content(kWh/kg) | Estimated power potential of unutilized fuel (GWh) |
| --- | --- | --- | --- | --- |
| Coffee husks | 162000 | 12200 | 4.61d | 56.2 |
| Bagasse | 887200 | 452000 | 5.25d | 2374 |

d Low heating value

It can be deduced from Table 1 that the agricultural industries generating these wastes can be electricity power self-reliant and capable of providing more power to sell out to the national grid. The excess power can also be supplied to nearby villages where grid extensions are untenable. Unfortunately, some of the industries are burning these fuels as waste for they generate more than they need for their power production and have no use of the surplus. These industries are mainly concerned with production of particular agricultural products and their missions do not include electricity power generation for sale. The industries, therefore, need some kind of enlightenment into energy production and investment opportunities, coupled with some incentives from the government that could support power generation enterprises.

Biomass, considered a renewable resource, is a common name for a variety of living and recently dead biological organic materials which have not been transformed by the geological process into fossil fuel [8]. Biomass can be combusted directly in furnaces (or biomass boilers) to generate heat energy, which can be converted into electricity through steam turbines driving electricity generators. Steam turbines are utilized in large plants such as in sugar mills, and their applications are not desirable for capacities below 1 MW. Biomass can also be gasified to generate producer gas which is used as fuel in IC engines, GT, furnaces and boilers. The use of biomass gasification technology in power production can permit attainment of considerable electrical efficiencies in the range of 30-48% especially where co-generation and/or steam injection is implemented. Applications in small scale capacities below 1 MW are desirable for rural settlements compared to conventional steam turbine systems where costs and technical issues become prohibitive [9]. When

gasification technology is implemented without co-generation, the efficiency of the power plant can drop to below 25%. However the drop can be offset by the low cost fuels, which can enhance the plant economic viability.

The sighted levels of efficiencies and the known low prices of biomass fuels, mostly from agricultural, municipal and timber mill waste streams, are some of the reasons that have stimulated interests into biomass gasification technology. This technology can be developed for electricity power generation in the urban and rural settlements and for small scale industries where biomass fuel availability can permit. Investments in biomass gasification technology find support through donations, tax waivers and subsidies. Such projects are also deemed environmentally friendly (clean technology) and industries seeking more carbon credits through the Kyoto Mechanisms can support, economically, biomass power plant projects in the developing countries.

Utilization of locally available biomass residues as primary energy source for village power plants in Uganda would be attractive for many reasons. It would reduce the need for importation of fossil fuels for electricity generators, and also improve on local self-reliance. It can also facilitate donor financing. The choice of the technology is not obvious however; for larger biomass power plants above a few Mega-Watts, steam turbine power plant is the obvious solution, but for smaller capacities this is not economically favorable as mentioned earlier. In Uganda, use of gasifiers to generate a combustible gas that can power IC engines driving electricity generators are being discussed for capacities in range of 25 —250 kWe. Pilot projects have so far seen some units installed in that capacity category, but the system is experiencing operational and technical challenges.

This study focused on the utilization of biomass for substitution of fossil fuels in the electricity power generation for isolated rural settlements and small scale industries in Uganda. The main emphasis is on the gasification of wood and agricultural residues, which besides it availability, affords a net zero carbon input to the environment when utilized in a sustainable manner [10]. Therefore, measures to improve on consumption efficiency and operating characteristics of equipment utilizing woody and non-woody biomass products for energy production is inevitable.

1.2 Objective of the study

1.2.1 General objective

The major research goal was to investigate the problems of biomass gasification technology applications with IC engines and GT. Emphasis was made on evaluating the product gas quality with the view of understanding their contribution to gasifier-engine performances in small scale isolated electricity power generation. This was to contribute new knowledge on issues where the knowledge available in the open literature about the performance and design constraints for small biomass fuelled power plants using externally fired gas turbines (EFGT) or IC engines was considered insufficient for decisions about the direction of further research on these

technologies in Uganda. The researched aimed at the development of indigenous capacity for designing and manufacturing of the gasification/combustion/gas-treatment equipment for small scale biomass fuelled power plants.

1.2.2 Specific objectives

The scope of the studies carried out in this first part of the research work was to a large extent determined by the availability of facilities for experimental research in Uganda and Sweden. In Uganda, the existing power plant with a gasifier and an IC engine delivered by an Indian company to a remote tea estate in western Uganda appeared to offer possibilities for studies of the field performance of such power plants. In Sweden, at KTH, the only operational facility that was considered useful for studies leading to the general goal was a very small downdraft gasifier with flaring of the gas. Opportunities for studies of updraft gasification in applications for externally fired gas turbines were offered by Lulea University of Technology.

The objectives of the studies focused on EFGT were to:

- Evaluate the technical performance characteristics of the externally fired gas turbine integrated with a biomass gasifier system.

- Identify design constraints for the high temperature heat exchanger required for the externally fired gas turbine

- Investigate the levels of alkali metal salts retention in an updraft gasifier and their carry over into the generated product gas stream.

The objectives of the studies focused on internal combustion engines with gasifiers were to:

- Determine if pelletized biomass can be expected to perform differently from wood pieces of the same size with respect to tar formation in a downdraft gasifier.

- Identify criteria for handling product gas samples drawn for tar analysis when using Solid Phase Adsorption (SPA) technique for sampling.

- Identify and propose solutions to current technical and operational problems being experienced by a 250kWe biomass power plant in Uganda,

- Evaluate the economic potential of the gasifier-IC engine and compare it to a diesel powered system

1.3 Conceptual Framework

Figure 1, shows an attempt to illustrate two energy conversion chains covered by this research, the fundamental problems associated with each technology and the research issues related to these. The two biomass fuelled technologies for electricity generation at a capacity below about 300 kW are competing with conventional diesel generators. In order to realize the biomass technologies either the tar problem for the IC-engine option or the alkali deposition problem for the gas turbine option must be resolved. Whether any of these two options will be competitive with the conventional option based on petroleum fuel depends on fuel prices, the investments required and the importance given to the efforts to reduce CO2-emissions from use of fossil fuels.

Figure 1: Conceptual frame work outline

The process for transformation of the solid fuel to biomass gas requires careful design of the gasifying unit and of the gas treatment process. The treatment of the gas depends on whether it shall be used in a gas turbine, or in IC engines applications. As a hot gas stream, it can be combusted under pressure to generate high temperature flue gas used in powering gas turbines, either directly or indirectly, after transfer of the heat to a pressurized air stream. Hot unclean gas application is associated with risks of deposition and corrosion in the turbine or the heat exchanger units. An approach using the EFGT system to remedy the issues of deposition in GT system is presented. Some performance evaluation of the EFGT system is discussed and some design issues related to the heat exchanger was studied. There are questions about whether deposition and corrosion shall occur in the heat exchanger used in the EFGT system instead. The occurrence of this scenario is partly described by a presentation on the alkali metal condensation on high temperature heat exchanger surface (see chapter 4 for details). Generation of a hot gas with low content of alkali metal compounds, choice of operating conditions that minimize deposition and corrosion problems, and hot gas filtration and methods for cleaning of surfaces where deposits have accumulated are key issues for this energy conversion route.

The cooling and cleaning of producer gas makes it suitable for IC engine application, but the condensing tars in the gas may lead to operational problems, or if separated from the gas may lead to environmental problems. Design of gasifiers that generate gas with low tar content and environmentally benign gas cleaning methods are key issues for this energy conversion route.

As explained above, the research presented in this thesis covers issues of importance for either the EFGT route or the IC-engine route and the selection of issues to study was to a large extent determined by the possibilities to carry out experimental studies with the available facilities.

The structure of the thesis is presented in the following section.

1.4 Overview of the Contents of the Thesis

In chapter 2, the state-of-the-art for the two biomass based energy conversion routes illustrated in Figure 1 is presented. The selection of research issues to be studied is discussed.

Chapter 3 discusses the design requirement for a heat exchanger for application in an EFGT system. The thermal model of the EFGT system and the heat exchanger design are discussed and the level of uncertainty in the design is pointed out. A unique feature to this chapter is the use of Monte Carlo simulation to provide possible design solutions to the heat exchanger design problem.

Unique results for alkali metal retention in an updraft gasifier are presented in chapter 4. Tests with wood pellets revealed that about 99% retention of the alkali species is possible. A thermodynamic modeling of product gas cooling in high temperature heat exchanger is carried out and the results of simulation of condensation reactions of K, Cl and S compounds are presented and discussed.

A study carried out to determine levels of tar yield from the gasification of wood cylinders and wood pellets is presented in chapter 5. The finding was that wood pellets generate more tar than wood cylinders of similar physical dimension; the reasons for this difference are discussed.

Chapter 6 presents another study carried out on tar samples taken from product gas in an updraft gasification process. The goal was to determine the level of deterioration of samples taken using solid phase absorption technique and stored for a particular period of time under different environmental conditions. The outcome suggests a need for inclusion of correction factors in samples analysis results when samples are stored in particular environmental conditions.

A case study conducted in a commercial biomass power plant is presented in chapter 7. The plant had experienced a 50% drop in power output, therefore was not delivering any substantial financial gain to the owners. This chapter presents the work carried to identify reasons for the drop in power output and the recommendations provided in order to get it up again.

Chapter 8 discusses the investment potential of biomass power plants in Uganda. The economics of installing and operating a 100kWe biomass and diesel power plants are compared. Results are presented which show biomass as a more profitable investment option in Uganda than a diesel system.

Chapter 9 offers a summary of the findings and suggests directions for further research aiming at development of indigenous capacity in Uganda for design and construction of the gasifier and gas treatment equipment for small scale biomass fuelled power plants.

References are listed in Chapter 10.

2. Developments in Biomass Gasification Technology

- A Brief Background

The first appearance of gasification technology found its way in the industries in the early 1920s' [11]. The technology gained prominence during World War II when petroleum fuel supplies were cut off to oil importing nations. At that time many gasifying units were built for automobiles and power production applications in industries. There is silence on the state of the technology after the war until the 1970s' when OPEC and other oil exporters increased oil prices [12]. The increase in oil prices rekindled interest in the technology development and application. Energy conservation approaches were implemented in most countries, which reduced the consumption of petroleum products between 1973 and 1980. Gasification technology was one alternative under development in some developing countries for power production and application in automobiles.

In 1981, oil prices went down when a decrease in demand and overproduction created surplus in the world oil market. After that year, the gasification technology development came to almost a halt until later, in the 1990s', when climate change related issues became a serious concern world over. Generally, commercialization of biomass gasification technology failed during the past decades for reasons of poor mechanical design, high gas tar content, improper tar cleaning methods, lack of training and unmet expectations and low oil prices, among others [12].

In some developing countries like China and India, developments in the biomass gasification technology started around the 1980s' with the focus of building up indigenous expertise in this field. To date, there are some commercial activities in this field, but the technology used is around the mid-1940s' level of automation in operation and performance. This means that plants cannot operate without a more or less continuous surveillance, and tar condensate resulting from gas scrubbing and cooling is not destroyed in the facility creating environmental hazard. The adaptation of gasifiers for different types of agricultural wastes, and the construction of equipment locally without careful design improvement considerations meant that the equipment do not meet the service requirements for smaller power plants in some parts of the world, such as in Western Europe, or North America.

- Thermal Gasification of Biomass

In the developing countries, the traditional methods for charcoal production through pyrolysis process realize yields of charcoal of about 20% or less of the loaded raw biomass material, and modern industrial technology offers yields of only 25-37%. [13]. Wood fuels, depending on their chemical compositions, have heating values in the ranges of 18.5-21MJ/kg. When compared to charcoal yield of 25%, with HHV at 30MJ/kg, the energy lost in the charcoal making through pyrolysis is in the range of 58-63% of the total raw wood energy. Therefore, solid biomass fuel transformed into gaseous fuel through a thermo-chemical process offers some advantages among others: higher burning efficiency, easily controllable and adjustable energy output, simpler burner construction, reduced levels of particulates emissions, direct application in IC engines, less fouling in heat exchanger equipment, possible gas storage and distribution within

short distances with less loss of energy in the process, good control of process temperature and better efficiencies can be realized from its utilization [14] [15] [16].

Gasification of biomass is a thermal decomposition in limited supply of the oxidizing agent (in this case air and/or steam) such that complete combustion does not occur. The process of biomass gasification can be described by Figure 2 and it is explained in the following sections. The stratification of the process is a better way of conceptualizing gasification process; otherwise the reaction process occurs almost everywhere within the fuel bed in the gasifier where temperatures are suitable.

Figure 2: Conversion of biomass into producer gas. Source:

http://www.members. tripod. com/~cturare/pro.htm

2.2.1 Gasification process

Gasification of the fuel usually is initiated by introduction of a burning medium or flame into the gasifier to start the biomass fuel combustion process at the oxidation zone (explained later in this section). The heat generated in the combustion process is used in the gasification. The mechanism occurs through the following processes of; drying, pyrolysis, oxidation and reduction.

Drying of the fuel occurs by heat generated in the exothermic reactions taking place in the gasifier. The fuel, depending on the gasifier type employed, have varying moisture content between 5-35% and these moisture is released as steam in the drying process. Drying occurs in the temperature range of about 100-150oC.

Pyrolysis is an endothermic reaction process occurring in limited supply of the oxidizing agent where volatiles from the raw biomass fuels are released. The process starts at low temperature from about 150oC and continues up to about 700oC where organic volatiles from the solid fuels are released leaving char/charcoal with other trace elements in solid form [17]. Thus, three products are usually generated in the process; pyrolysis oil (tar) mixed with condensed water, char and gas, with all having relative proportions depending greatly on the pyrolysis method, biomass fuel composition and on the reaction parameters which relate to the reactor design. Some of the gas and char realized in the pyrolysis process are partly consumed in the oxidation stage of the gasification process to generate more heat to sustain the endothermic processes.

Oxidation is the exothermic reaction between the biomass fuel and air (or air and steam) which gives more heat to sustain the gasification process. Part of the volatiles and char realized from the pyrolysis process are also combusted to generate the required heat for the gasification process. The reaction usually takes place between 700oC to 1300oC, depending on the gasifier type and the operating performance required.

In the reduction process which occurs at temperatures between 800-1100oC CO2 and H20 are partly reduced into CO, H2 and CH4. Other volatiles from the pyrolysis process are also reduced to increase on the content of the gases with some escaping and condensing as tar in the gas treatment units. The hot char bed created act as a catalyst in breaking down the heavy hydrocarbons into CO and H2 molecules. The process efficiency in tar cracking depends on the gasifier design and reaction temperatures. Tar is the result of un-cracked (unreduced) hydrocarbons which proves very troublesome in some downstream equipment in the biomass gasification technology application for power production.

Solid biomass fuel contains C, O, H, S, N, and traces of other elements in different proportions depending on the biomass source. Its gasification carried out in limited supply of an oxidizing agent (in this case air in sub stoichiometric ratio of 1.5:1-1.8:1) generates gaseous mixture (producer gas) and ash residues. Producer gas is constituted of H2, CO, CH4 and traces of other hydrocarbons, which form the combustible entity; CO2, H2O(g) and nitrogen N2 forming the incombustible part. Producer gas contains these compounds in proportions depending on the gasification conditions and the raw biomass fuel chemical composition.

2.3 Gasifier types

There are many different types of gasifiers that are used in the gasification of biomass for heating applications and powering of mechanical prime movers. Depending on the gas application requirement, raw fuel characteristics, and available funds: it is possible to obtain the best gasification technology available. Normally, options are limited by the financial implication of the required investment. The general types of gasifiers include; fixed bed (downdraft, updraft), fluidized bed and entrained bed. Downdraft and updraft gasifiers are studied in this work due to the relatively low costs in their construction and in operations.

2.3.1 Downdraft gasifiers

Downdraft (co-current) gasifiers get the name from the producer gas flow which moves downward in the direction of flow of the solid fuel. The raw fuel is usually fed from the upper part of the gasifier and air is delivered at the combustion zone where combustion is first initiated- shown in Figure 3. The gasification process in downdraft gasifiers starts with the drying of fuel by heat of combustion sustained in limited supply of air passing through the system. Closure to the combustion zone the pyrolysis process is very effective in releasing combustible volatiles from the solid fuel to support the combustion process whose products (CO2, H20 and other volatile organic compounds) are reduced in the reduction zone into CO, H2 and CH4 and tar.

Pyrolysis zone

Combustion zone

Figure 3: Downdraft gasifier

The producer gas realized contains less of the volatiles generated in the pyrolysis process since a considerable amount of the volatiles are oxidized while passing through the combustion zone and are subsequently reduced to producer gas with some escaping as tar vapor.

Typical producer gas compositions obtained from wood and charcoal with 20% and 7% moisture content, respectively from a downdraft gasifier are shown in Table 2 in the next page.

| Component | Wood Gas (vol. %) | Charcoal Gas (vol. %) |
| --- | --- | --- |
| Nitrogen | 50 - 54 | 55 - 65 |
| Carbon monoxide | 17 - 22 | 28 - 32 |
| Carbon dioxide | 9 - 15 | 1 - 3 |
| Hydrogen | 12 - 20 | 4 - 10 |
| Methane | 2 - 3 | 0 - 2 |

Table 2 : Producer gas composition from Wood and Charcoal gasification in downdraft gasifier

Source: FAO Forestry Paper-72, T0512/E 1986 (http:jjwi

ww.fao.or

irgjdocrepj t0512ejt0512e09.htm)

From Table 2 above, it can be seen that a large proportion of producer gas is constituted of N2 from the air used in the gasification. This is because when using air as the oxidizing agent, every 1 part of oxygen in the air consumed by the fuel, 3.76 parts of N2 accompanies it. N2, being incombustible, dilutes the producer gas lowering its energy per unit volume with the resultant low LHV. This value is in the range of 4 — 6 MJ/Nm3 depending on the process being used with air. When steam or oxygen is used as the oxidizing agent, the LHV can be improved to over 10 MJ/Nm3. The LHV of producer gas when compared to those of other fuels such as natural gas and gasoline with values of 31.6 MJ/Nm3 and 34.8 MJ/Nm3, respectively is found to be very low. A book by FAO on producer gas application with IC engine using a down draft gasifier mentioned that the gas-air mixture has heating value of about 2500 kJ/m3 while the stoichiometric gasoline-air mixture has about 3800kJ/m3 [18]. Though the conditions under which this values were determined is not mentioned, the implication could be that an IC engine powered by gasoline when converted to run on producer gas is likely down-rated to 65 % of its original power output.

2.3.2 Updraft gasifiers

In updraft gasifier, shown in Figure 4, the generated producer gas flows in the opposite direction to the solid fuel flow (a reason it is sometimes referred to as a countercurrent gasifier).

Figure 4: Updraft gasifier. Source: http://wwww.knowledgepublications.com

The combustion process with limited supply of air creates a reduction zone (zone with hot pyrolyzed char) just above the combustion front which reduces the generated CO2 and H20 into mainly the CO, H2 and CH4. The high temperature gas moving through the fuel bed pyrolyzes the fuel just above the reduction zone and entrains the pyrolysis volatiles with it to the gas outlet. The resulting producer gas stream contains higher percentages of other low molecular mass hydrocarbons than realized in downdraft gasification process. The result is that the producer gas is exited at a lower temperature than in downdraft process, but with the updraft process having the advantage of a better thermal efficiency.

The main drawback of updraft gasification is the high tar content in the producer gas generated. This render it not suitable for applications with IC engines where low costs investments are concerned such as in rural villages of Africa. The higher heating value of the gas realized from the updraft gasifier makes it suitable for thermal applications such as in firing kilns and for applications with EFGT system. The heating value is a result of entrainment of the volatiles generated by the pyrolysis process, which enhance the producer gas LHV.

2.3.3 Fluidized bed gasifiers

Fluidized bed gasifier shown in Figure 5, has the bed consisting of inert entities such as sand and sometimes a catalyst which is heated up externally to about 700oC. Biomass fuel is added into the heated bed, and the oxidizing agent is passed through the distributor plate. The bed temperature is usually maintained between 700-900oC in order to avoid slagging in the bed. The oxidizing agent, commonly oxygen, air and/or steam, is blown upward through the fuel bed at sufficient velocity to permit particles elutriation.

Figure 5: Fluidized bed gasifier. Source: FAO I18l

There is proper mixing between the biomass fuels, the hot bed material and combustion gases creating a uniform temperature distribution in the gasifier. Fast pyrolysis of the fuel occurs with the generation of large amount of gas. Further gasification and tar cracking occur in the gas phase. Usually an internally built cyclone separator minimizes the amount of char and ash particles blowout, but some particles are still entrained in the gas stream which may require further gas cleaning-depending on the application at hand. Fine fuel particles are preferred in this type of gasifiers, and the gasifiers are suitable in the capacities above 10MWt [19].

2.3.4 Entrained flow gasifier

In an entrained flow gasifier shown in Figure 6, pulverized fuel is fed using an inert gas under pressure, typically 20-50bar, in a burner inside the gasifier. Pure oxygen is the oxidant often used in this gasifier. Thermal reaction occurs at temperatures in range of 1300-1500oC resulting into a producer gas rich in CO and H2, and with no tar. There are two types of this gasifier, i.e. slagging and non-slagging entrained flow gasifiers.

Figure 6: Entrained bed gasifier. Source: www.netl.doe.govl...lgasificationlbasicsl4.html

In the slagging type high temperature causes ash melting. The molten ash is allowed to condense on the inside wall of gasifier to form protective solid coating of slag. While in a non-slagging type the maximum acceptable ash content in the raw fuel is 1%, therefore ash melting is not present. The ash is produced as very fine dry fly ash. A certain quantity of soot often is purposely produced to generate condensation surface in the gas to prevent fouling of the gasifier wall.

2.3.5 Some Aspects on Applications of Gasifiers

Table 3 gives a summary of the different gasifier types and their characteristics. Fluidized and entrained bed gasifiers are suitable for large scale applications. Fixed bed (Downdraft and updraft) gasifiers can find applications even below 100kWt with no serious penalty on performance, which makes them suitable for small scale applications.

Table 3 : Characteristics of different gasification configurations (source, www.bgtworld.com)

| Fixed bed | Fluid beds | Entrained beds |
| --- | --- | --- |
|  | Co-current | Counter current | Dense | Circulating |  |
| T°C | 700-1200 | 700-900 | <900 | <900 | 1500 |
| Tars | low | very high | intermediate | intermediate | absent |
| Control | easy | very easy | intermediate | intermediate | very complex |
| Scale | < 5MWt | < 20MWt | 10 <MWt< 100 | 20 <MWt <? | >1 00MWt |
| Feedstock | very critical | critical | less critical | less critical | very fine particles |

Compactness and porosity of the fuel bed are critical issues for a balance between reaction control process and heat transfer control process in the gasification of the biomass fuel in fixed bed gasifiers. This is because fixed bed gasifiers have very low heat and mass transfer between solid biomass and the oxidizing agent.

Feed stock requirement for downdraft gasifiers is more stringent compared to updraft, and the yield of tar is highest in the latter. Improved performances with downdraft gasifiers can be realized with relatively dry fuel of moisture content below 20% by weight. On the other hand, Moisture content in updraft mode can reach up to 50% and with no particular demand on fuel size and shape. Application up to 20 MWt is possible in updraft mode and this figure reduces to about 5 MWt in downdraft mode. These are some of the remarkable differences that allow the adaptation of updraft and downdraft gasifiers to particular applications. The influences of other characteristics of the fuel such as size, shape and structure on performance of the gasification process are discussed in a review on the gasification of biomass [20] [21].

Another review, with particular emphasis on contemporary issues in the thermal gasification of biomass, discussed recent advances in the technology and the producer gas utilization [22]. Table 4, an extract from the review, provides some critical technical issues associated with the production and application of producer gas including the advantages and the disadvantages of the three major types of gasifiers discussed in section 2.2.1. According to Table 4, the pressurized gasification process is costly in small scale applications. The heating value of the gas increases with use of oxidants in the order, air > steam > oxygen. Fluidized bed gasifiers are economically favored in large scale applications and offers high gas output, but with high yield of particulate dust.

Table 4 : Advantages and challenges of gasifying agents, gasifier design and gasifier operations t22]

|  | Main advantages | Main technical challenges |
| --- | --- | --- |
| Gasifying agents: |  |  |
| Air | 1. Partial combustion for heat supply in gasification | 1. Low heating value (3-6 MJ/ N m3) |
|  | 2. Moderate char and tar content | 2. Large amount of N2 in syngas |
|  |  | (e.g., 450% by volume) |
|  |  | 3. Difficult determination of ER |
|  |  | (usually 0.2-0.4) |
| Steam | 1. High heating value syngas (10—15 MJ/N m3) | 1. Require indirect or external heat supply |
|  | 2. H2-rich syngas (e.g., 450% by volume) | for gasification |
|  |  | 2. High tar content in syngas |
|  |  | 3. Require catalytic tar reforming |
| Carbon dioxide | 1. High heating value syngas | 1. Require indirect or external heat supply |
|  | 2. High H2 and CO in syngas and low CO2 in syngas | 2. Required catalytic tar reforming |
| Gasifier Design: |  |  |
| Fixed | 1. Simple and reliable design | 1. Long residence time |
| bed | 2. Capacity for wet biomass gasification | 2. Non-uniform temperature distribution |
|  | 3. Favorable economics on a small scale | in gasifiers |
|  |  | 3. High char or/ and tar contents |
|  |  | 4. Low cold gas energy efficiency |
|  |  | 5. Low productivity (e.g., 5GJ/m2 h) |
| Fluidized bed | 1. Short residence time | 1. High particulate dust in syngas |
|  | 2. High productivity (e.g., 20-30 GJ/m2 h) | 2. Favorable economics on a medium to |
|  | 3. Uniform temperature distribution in gasifiers | large scale |
|  | 4. Low char or/ and tar contents |  |
|  | 5. High cold gas energy efficiency |  |
|  | 6. Reduced ash-related problems |  |
| Gasifier operation: |  |  |
| Increase of | 1. Decreased char and tar content | 1. Decreased energy efficiency |
| temperature | 2. Decreased methane in producer gas | 2. Increased ash-related problems |
|  | 3. Increased carbon conversion |  |
|  | 4. Increased heating value of producer gas |  |
|  | 1. Low char and tar content | 1. Limited design and operational experience |
| Increase of | 2. No costly producer gas compression required for | 2. Higher costs of a gasifier at a small scale |
| pressure | downstream utilization |  |
| Increase of ER | Low char and tar content | Decreased heating value of syngas |

Fixed bed gasifiers are the simplest modes of gasifiers to construct with less equipment investment, easier to operate and to maintain. These attributes, of fixed bed gasifiers, are suitable for anticipated use in the isolated rural settlements in developing countries. The most common of this category are the downdraft and updraft gasifiers for which some performance indicators were studied in this work.

2.4 Contaminants in the Producer Gas

2.4.1 Tar in producer gas

Tar can be defined as condensed organic compounds with boiling points higher than benzene [23]. It is still the critical constraint in biomass gasification technology applications for power production with IC engines applications. In biomass gasification, the pyrolysis process generates considerable amount of primary tar. As temperature is raised above 5000C, primary tar begin to transform in to more gas and a series of molecules called secondary tar which are formed depending on the severity of the temperature [24] [25]. In downdraft and fluidized bed gasifiers, some

of the pyrolysis gases are combusted to give more heat required in the oxidation stage for the formation of producer gas in the following reduction process. The process must be taken to about 700 — 900oC to break primary tars down to smaller amounts of secondary tars and more gas, typically 1-5% secondary tar in the gas are cracked in this way. Normally a catalyst would be required to lower this secondary tar level further at these temperatures (700-9000C) [26] [27]; otherwise gas cleaning processes are essential to remove tar from the producer gas. Tar generation in biomass gasification is so depended on the type of gasifier used and on the biomass fuel characteristics (refer to Table 4 for details of particular gasifier tar output). The order of tar yield quantities by the different gasifier types is: Updraft >Entrained bed >Fluidized bed > downdraft. According to some authors, a gasifier that yields more than 500 mg/Nm3 of tar in a producer gas cannot be suitable for coupling with IC engines. For a worst case scenario, a gasifier producing 2 g/Nm3 (0.2%) tar equates to about 2g of tar per hp-h (2 kg per 0.746 KWh) [28]. Thus, applications where tar content in the producer gas can cause problems would necessitate that gas cleaning is effectively done. The cleaning can start from the choice of the gasifier. For instance, a downdraft gasifier with its low tar yield is a suitable producer gas generator for application with IC engines.

Use of water scrubbers in tar gas cleaning

The stringent service requirements for most producer gas fired prime movers and other secondary processes calls for new effective and efficient gas cleaning approaches. Some of the methods used to remove tar from the producer gas are discussed in this section. Small scale biomass gasification gas engine power plants, especially those built in developing countries, are using water scrubbing, porous biomass bed and fabric filters for gas cleaning. The method employed is simple in construction and to maintain, which makes it economically favorable in developing countries. A large number of gasifiers from the Indian manufacturer Ankur-Scientific use this gas cleaning method [29]. A suitable gas quality is achieved by the process in small plants mostly of capacity below 500 kWt. Nevertheless, tar cleaning through water scrubbing and condensation is of great environmental concern because tar separation and destruction is not catered for in the simplified cleaning process. Known methods of tar separation from water are very costly and some are limited in function. Some of the tar entities like phenols are poisonous and appreciably soluble in water. This means more appropriate waste water treatment process is mandatory, otherwise the poisonous compounds may end up in public utility water system.

Use of catalyst in tar cracking

A lot of work is going on in studying catalytic biomass gasification of which some are presented here.

One report gives an extensive literature review on evaluations carried out with dolomite, alkali metals and nickel as catalysts for elimination of tar in the producer gas [30]. Dolomite is cheap and easily renewable and can achieve almost 100% tar removal. It is best performing when calcined, or with addition of iron oxide and suitably used as primary catalyst in the bed for heavy tar removal. Carbon deposition and attrition causes deactivation of dolomite which calls for regular renewal. Alkali metal catalysts are used mostly as primary catalysts since application as secondary

catalyst do not achieve 80% conversion of tar. They are resistant to carbon deposition and increases rate of gasification tremendously. The catalysts are non- recoverable and costly, their presence in the ash can cause particles agglomeration (ash melting) in the bed at certain temperatures. Nickel catalysts are very effective in removing tar from the producer gas and in adjusting the gas composition. It is used as secondary catalyst mostly with dolomite as a primary catalyst to eliminate coking. It is cheap and commercially available. Deactivation occurs due to nickel particle growth and coking.

Another study on recent advances in hot gas cleanup by use of catalysts was reported on some of the catalysts under tests in laboratory scale, pilot and demonstration plants [31]. Catalytic reaction mechanisms and models used to simulate contaminants in the producer gas are presented. Some findings are that calcined dolomite, though effective in removing tar, is very soft and fragile; this limits its application in some types of reactors such as fluidized bed reactors. Deactivation of nickel and ruthenium catalysts supported on alumina can be prevented by use of steam injected with producer gas into the catalytic reactor and the use of non-alumina catalyst promoters. Steam causes gasification of carbon deposits in the reactor. The report concluded that hot gas cleanup catalysts and processes, with exception of particulate cleanup, have poor performance and limited use in full scale biomass gasification plants, therefore more research is need.

2.4.2 Tar treatment methods in selected biomass gasification technologies

The plant utilizes an IC engine for power generation. Raw fuel is dried and pyrolyzed in a screw

Some of the pilot projects and demonstration plants have devised different methods for gas cleaning especially for use in gas engines. The methods are described for the different facilities in this section of the work.

Two stage gasification process

A two stage gasification process has been developed by the Technical University of Denmark, shown in Figure 7. The gasifier was called Viking, and it is considered suitable for CHP application [32].

Figure 7: Two stage gasification process [ 1

reactor heated from outside using the exhaust gas from the engine. Partial oxidation of the pyrolysis gas takes place in air at about 1100oC. The high temperature causes some tar to crack; the rest is carried into the hot char bed where they are transformed into more gases. Tar content of the producer gas is less than 5mg/Nm3. The pilot plant, completely automated, with 75kWt power input has electrical efficiency of about 25%. The plant, which is scalable, is estimated to attain efficiency of 37% on scale up from 0.2 to 2MWe, and work continues at DTU, in Lyngby, on performance improvement on the two stage gasifier [33].

OLGA gas cleaning process

In the Netherlands ongoing research into producer gas tar cleaning method based on gas scrubbing using organic oil has been developed [341, [35]. The method known as OLGA is a highly efficient tar removal approach which operates above the water dew point. A schematic drawing of the process is presented in Figure 8. Tar removal principle is based on a multiple stage scrubber in which the gas is cleaned by special scrubbing oil. After successful tests of the method in a laboratory size and pilot plant, a demonstration plant was built in Moissannes, France. The plant with a fixed bed gasifier of 4.0MWt power output was tested for 100hrs with the resulting gas output of 2000Nm3/h. The gas was used to run a gas engine-generator set delivering 1.1MWe. Tar was completely eliminated from the gas and dust level was below detection limit. The advantages offered by this plant are that no fouling in the system occurs due to tar condensation, and water treatment issues are completely avoided with the use of oil scrubbing.

Figure 8: OLGA gas cleaning process [ 1'

Biomass fuels used included wood saw dust and wine press residues. Investment needs are high for the small plants, equivalent to about 3500U$ SEK / kWe for 100kWe plant. In large plants the specific investment is estimated to be substantially lower at about U$400/kWe at 2.5MWe.

VTT nickel based catalytic reactor process

Another technique for gas cleaning was tested on a smaller scale by VTT in Finland and has been demonstrated in Kokemaki, Finland shown in Figure 9. Some of the operation data of the plants are presented in Table 5.

Figure 9: Carbona Gasifier and gas cleaning technology [ ]. Table 5: VTT Demonstration plant

| Kokemaki |
| --- |
| Plant Type | CHP |
| Electricity Power (MW) | 1.8 |
| Thermal Power | 4.3 |
| Efficiency (%) | NA |

The plant with Fluidized bed gasifier and using tar reforming (catalytic tar cracking) process provides 1.8MWe and 4.3MWt for district heating. The electric power is realized from three gas engines each driving generators of 600kWe. The Ni-based catalytic reactor is operated at 900o C. Gas cleaning system also consists of a fabric filter and a scrubber where the gas is cooled to temperature of about 30°C. See Figure 9 for plant layout. The content of tar after the gas purification is less than 1 mg/Nm3 [36].

Hot commissioning was done at the beginning of 2007. VTT is proceeding with catalytic tar reforming, among other things, to study the effect of impurities in the fuel on the catalyst and to replace the Ni-catalyst with zirconium [33].

TARWATC process

Babcock & Wilcox Volund, in Denmark, has developed a gas cleaning process for their fixed bed updraft gasifier shown in Figure 10. The technology, demonstrated in a cogeneration plant at Harbore, is presented in a detailed report by Teislev [37]. Tar content in the unprocessed producer gas from the gasifier is about 60-80 g/Nm3. Two processes are used in the gas cleaning, and another for waste water cleaning.

In the first process of gas cleaning, instead of a water scrubber, a district heating and cooling heat exchanger serve as a condenser for the tar-water and particulates mix in the raw gas stream. The partially cleaned gas is passed through a second process with a wet Electrostatic Precipitator (ESP) where more tar-water mix and dust particles are separated from the gas. The waste from the condenser and ESP are collected and sent to an evaporator.

REACTOR

TARWATC process

TO FLUE STACK

HEAT EXCHANGER

LIGHT TAR BUFFER

WASTE WATER INLET

t TO GASIFIER

HEAVY TAR

DH COOLER

ENGINE EXHAUST EXHAUST BOILER

EVAPORATOR SEPERATOR

37

Figure 10: Process for purification of tar condensate under Babcock & Wilcox Volund [ ]

Tar is separated from the mix in a coalescer, heavy tar is collected and can be used for; district peak load firing of water boilers, direct injection into gasifier combustion zone, and for gasification in a small gasifier. After the first two processes the tar and dust content in the gas is reduced to about 25 mg/Nm3 with gas LHV of 5.6MJ/Nm3.The water and light tar mixture is passed through a purification process using a method called TARWATC developed by Babcock and Wilcox Volund.

In the third process contaminated water is heated, by boiling water from the exhaust gas boiler, in an evaporator generating steam and leaving light tar (combustible liquid) which is collected and re-injected into the reactor, or used as fuel additives for heat production. The lightly contaminated steam generated is heated by clean steam from the reactor in a counter flow heat exchanger. The heated contaminated steam is sent into the reactor where combustion occurs cracking the remnant tar giving out clean steam.

Dual power gasification process

AIR	|

rl

A Finnish company, Entimos Ltd, has developed a fixed bed gasifier which is a combination of downdraft and updraft gasifier illustrated in Figure 11. Producer gas is released at two levels; an upper level giving out gas with relatively high tar content for application in direct combustion, and a lower level that provides a tar free gas after the particulate filter treatment for use in gas engine operation [38]. A demonstration plant of 470 kWe / 1130 kWt has been installed at Lestijarvi and was commissioned in March 2007. An overall efficiency of 81.5% has been achieved with this gasifier, but the gas quality issues still remain unresolved.

Figure 11: Dual power gasifier for the production of low tar and high tar content producer gas installed at Entimos Oy, Finland [ ]

2.4.3 Alkali metals in producer gas

Alkali metals occur naturally in raw biomass fuel as trace metals. The metals are vaporized during the gasification process and form compounds which are entrained in the generated producer gas stream. Their entrainment in the gas stream is very detrimental to the service life of the downstream equipment.

It is known that at higher temperatures of above 800oC in the gasification process the alkalis (especially, some compounds of Na and K which are the most problematic) are in vapor form [39], and their entrainment quantity in the gas phase in the gasification process is not known, and whether they are entrapped in the fuel bed and later transported to the ash bed there is no literature available. But it is known that in the vapor phase the alkali metals form compounds. These compounds on entering regions of low temperatures in GT and heat exchanger surfaces, condenses. When surfaces are at relatively low temperatures (of about 500oC) the condensate turn into solid salt deposits, and at slightly higher temperatures (600-700oC) they condense into liquid salts. The buildup of the solid salt deposits causes clogging in turbine recesses and imbalances in the rotating parts of the turbine, while the condensed liquid salts causes hot corrosion on turbine blades.

Low producer gas output temperature from some gasifier types are the reason to speculate for the possible retention of the alkali metals in that gasifier; other reasons are not clear, and the uncertainty prompted a study to establish the extent of the alkalis retention in an updraft gasifier intended for application with EFGT system.

Reduction of the alkali metals entrainment in the producer gas stream can be achieved by utilizing gas cooling and cleaning methods, or by use of gasifiers that can allow almost 100% retention of the alkali metals. Updraft gasifiers have been identified for studies relating to the retention of alkali metals in them; see Chapter 4 for details on retention of the alkali metals in updraft gasification process.

2.4.4 Particles in producer gas

A lot of particles is generated and are entrained in the producer gas during biomass gasification process. The constituents include among others, ash, char and soot to a limited extent. Ash is mainly consisted of inorganic compounds of the alkali metals, sand and unburnt carbon. Ash melting in the gasifier interrupts the gasification reaction process with the result of yielding poor quality (less energy content per unit volume than normal) producer gas, and possible burn-out of some auxiliary units in the gasifier can result. Normally, gasification must be carried out below ash melting points to avoid ash bed slagging.

The entrainment of ash particles in the producer gas stream can lead to erosion in down steam equipment, and this is attributed to the abrasive nature of the ash particles constituents which to some extent is linked to the fuel contamination with soil. Hot gas filtration can be utilized in the gas cleaning process, but the process costs have caused many gasification projects to be decommissioned shortly after takeoff [26]. Normally, in a GT system the combustion chamber is integrated within the turbine housing. There are no problems associated with alkali metals compounds when running on natural gas and producer gas from coal gasification. But when operating on producer gas from biomass gasification, the alkali metal compounds deposition and the ash particles in the producer gas stream necessitate that rigorous cleaning is effected before utilization in GT.

Char particles are formed from un-burnt char from the pyrolysis process of the gasification and can be filtered from the gas stream by use of cyclone, water scrubbers, electrostatic and fabric filters. Soot is formed during the gasification process. It is constituted by agglomerates with a diameter of up to several hundred nanometers. These have a fine structure of spherical primary particles. Soot formation is initiated by the pyrolysis of fuel particles and the formation of polycyclic aromatic hydrocarbons (PAH). The most important precursor of the formation of higher hydrocarbons is acetylene (C2H2). 2-dimensional condensation processes follow, and finally a rearrangement produces spherical primary particles which continue growing at their surface [40]. The most concern is that that fine particles created in the process remain a serious toxicological problem.

2.5 Producer Gas Applications

2.5.1 Gas quality requirements

Producer gas can be utilized either as a hot or cooled gas stream depending on the intended application. Hot gas applications from updraft gasification process find use in GT and other thermal systems. The high tar content in an updraft gasifier process necessitates a significant investment in gas cleanup equipment, which renders it economically unfavorable for investments in gas cleaning to meet IC engine application in developing countries.

Tar and particulate loads from the different gasifier types are presented in Table 6. The figures presented are conservative and were determined based on different fuel and gasifier characteristics, and on particular gasifier operating parameters. As such different authors reported varying ranges for a particular gasifier, as quoted by Milnes et al [41]' As shown in Table 6, it cannot be overemphasized that downdraft gasifiers yield less tar compared to other types of gasifiers with estimated average of about 0.275g/Nm3 compared to about 55g/Nm3, 6g/Nm3, 19g/Nm3 in updraft, fluidized bed and entrained bed gasifiers, respectively. Thus, in downdraft gasification process less cleaning is involved for applications with IC engines compared to the other gasifying processes.

Hot producer gas has low density such that when used in IC engines the power output is significantly lowered due to the decrease in energy content per unit volume. Thus, downdraft gasification with low tar yield, provided with gas cooling and cleaning, is suitable for application with IC engines. There is obvious sacrifice of efficiency in form of heat loss in the gas cooling process.

Gas cleaning is expensive if done at high temperatures and leads to reduced efficiency if the hot gas is cooled before cleaning. An alternative approach is the use of external firing in GT system, which was introduced earlier as EFGT system. In this case, the turbine is driven by expansion of heated compressed air. The system is a favorable technology because its design reduces fouling load in the GT unit. The design simplicity makes it suitable in small scale application for power plants in rural and isolated settlements. The evasion of fouling in the GT unit is achieved by the relocation of the combustion chamber outside the turbine unit and the inclusion of a heat exchanger to handle the unfiltered gas stream.

There are two possible ways to using the EFGT system. One method involves biomass combustion directly in a chamber integrated to a heat exchanger, and the other constitutes biomass gasification and the subsequent combustion of the generated producer gas in a detached combustor. In both cases the heat of combustion is transferred to compressed air through a heat exchanger and the heated air is then expanded in the turbine unit. A report on experiments carried out by Talbott's Heating Ltd. in England presented the use of direct biomass combustion integrated with a heat exchanger for powering a micro-gas turbine [42]. Though the system showed good performance with electrical efficiency of about 17%, there is no mention about clogging and fouling of the heat exchanger in the system.

The EFGT system affords some advantages over the directly fired system including; clean working fluid (air) in the turbine, better temperature control with producer gas and inclusion of an external combustor allowing for low pressure operations with increased efficiency [43].

The main reason alkali metal salts end up in the gas phase when biomass is gasified is that many compounds of K and Na are transformed into vapor phase at temperatures in the range of 700- 8000C and above [44]. This volatized compounds ends up in the producer gas stream. Up-draft gasifiers have producer gas temperatures in the range of 150 — 2500C and it can be expected that the producer gas generated may have very low alkali metals content [45]. This is anticipated to reduce on deposition and corrosion problems in a high temperature heat

exchanger used in an EFGT process. However, it appears that so far no one has studied the fate of alkali metal compounds generated when biomass is gasified in an updraft gasifier.

To this moment it is clear that the technical challenges with the producer gas relates to the quality that should be suitable for applications in IC engines and GT. These challenges are more pronounced in the small scale biomass power plants [46]. Table 6 shows the recommended gas quality for GT and IC engines. In Table 7, it is shown that in the directly fired GT system particulate loading of up to 15 mg/Nm3 is acceptable for sizes less than 20 [im. While with EFGT there are no particulates limit and no concern with tar. The presence of tar in the hot producer gas for EFGT system application increases the energy density of the gas. Requirement for IC engines shows that about 20 mg/Nm3 of particulates in the producer gas is are acceptable, and the limit of tar loading of up to 0.5 g/Nm3 is recommended. These figures are recommendations since there are no standards for gasifier designs and operations.

Table 6: Gas quality requirements for gas turbines and IC engines I27l I47l

| Power source | Gas Quality |
| --- | --- |
|  | Particles | Tar | Gas temperature | Na + K |
| Directly fired | 15 mg/Nm3 | No concern when tar condensation is | See comment a | 0.1-0.2 |
| GT | ( 20 - 5 [im)b | avoided |  | mg/Nm3 |
| Externally fired | Data missing | No concern with tar noted |  | Data missing |
| GT(EFGT) |  |  | < 600-700°C |  |
| IC engine | 5-20 mg/Nm3 | 1 mg-0.5 g/Nm3 | < 40 oC | Low levels with cool gas |

- For pressurized gasification a compressor is not need prior to combustion chamber. If a compressor is needed then the lowest possible temperature of the gas is required before compression to minimize compressor work.

- Preferably no particles above 20[m. For particles below 5[m can be up to 100 mg/Nm3 accepted P6].

Table 7: Different gasifier Tar and particulates loads t47l

|  | Tar (mg/Nm3) | Particulates (mg/Nm3) |
| --- | --- | --- |
| Updraft | 10,000-100,000 | 100-1,000 |
| Downdraft | 50-500 | 100-8,000 |
| Fluid bed | 2,000-10,000 | 8,000-100,000 |
| Entrained bed | 8,000-30,000 | 30,000-100,000 |

o Distinguished two basic types of tars: Oxygenates and PNA

2.5.2 Cooled gas for IC engines applications

Producer gas is subjected to careful cleaning and cooling in order to meet the application requirement for IC engines as shown in Table 6. Particles in the gas stream increases wear and tear, while tar may cause clogging of the intake manifolds and on the valve seats. Abrasive particles can cause costly damages in the cylinder bores and on piston rings. Clogging can lead to significant loss in power output of the engine. These detrimental entities in the gas are formed from condensation of organic compounds and entrainment of ash particles in the gas stream. Tar filtering is still a major challenge in the gasification industry since costs and environmental

concern are eminent issues to address. In a report by Milner et al [41], many different studies on gas quality related issues provided the acceptable limits for ash particles of about 0.5-20mg/Nm3 and for tar in the range of 0.5-100 mg/Nm3. This report had no details on conditions under which these quality criteria were arrived at. It is also not known whether current technology improvements in engines can permit higher tolerance levels for tar and ash particles. This would call for the documentation of operating experiences with the new equipment for more understanding of improvement measures to incorporate.

A simplified biomass gasification integrated with an IC engine scheme is shown in Figure 12 below. In this process course particles are separated by a cyclone filter.

Figure 12: Biomass-gasifier IC engine system

In a small scale biomass gasification power plant for IC engine application, condensable organic matter and ash particles are filtered from the gas stream through different combinations of the following processes:

- Cyclone to remove coarse particles

- Scrubber for removal of tar, some dust particles and gas cooling

- Catalytic tar cracking units

- Course filters made of packed beds of porous materials

- Fine filters made from fabric material for removal of very fine particles.

Catalysts are not utilized in most biomass gasification plants in developing countries. In a typical small scale biomass gasification plant application with IC engines, the producer gas is cooled to about 35oC. Cooling of the gas increases its density, which effect an increase in the engine power output. However, cooling lowers the system thermal efficiency and increases need for waste water treatment. As an example, scrubber water contains poisonous entities, e.g. phenols, which must be removed before the water is drained in to the natural water stream.

Though gas cleaning reduces tar load to the engine, few hours of shut down for maintenance activities every month is inevitable. Clogging, caused by tar, is greatly reduced when petroleum fuel is used in the last 10 minutes to engine shut down [36].Particles separation from the gas stream has not been a serious challenge in the application of biomass gasification technology, and therefore methods of gas cleaning for particles are very successful. The particulates filters can be packed beds of raw biomass fuels or sand/gravel bed connected in series and to a fabric filters for final fine dust removal. The scrubber can use oil or water scrubbing depending on the technology utilized in the gas cleaning.

Tar cleaning can involve the use of a catalyst mixed with fuel (primary catalysts) in the gasifier for tar cracking; others employ a separate reactor packed with catalyst (secondary catalysts) at elevated temperatures of about 600oC where the producer gas is passed for tar cracking. See section 2.4.1 for details on producer gas tar cleaning technologies.

2.5.3 Hot gas for turbine application

In a conventional GT system, the combustion chamber is positioned between the compressor and the turbine unit. The turbine is driven by hot combustion product i.e. flue gas. A scheme for a GT process integrated with a gasifier is illustrated in Figure 13. Particulates and corrosive species carried in the flue gas can lead to failure of the turbine unit.

Direct combustion in the turbine unit causes deposition and corrosion experienced with use of biomass fuels that contain some inorganic species. The malign compounds are alkali metal salts and the abrasive ash particles entrained in the gas stream. The effects of deposition and corrosion are more devastating in small GT, and are the reasons for the slow development of GT application with producer gas in small scale capacity ranges. For instance, a tests carried out on one Rover IS/60 gas turbine, with a modified combustor for producer gas and using direct firing, revealed that alkali metal compounds and ash in the gas stream caused the turbine engine to clog within 15 to 30 minutes of test run [48].

The application of producer gas from biomass gasification for direct firing with of GT system require that cleaning of the gas between the gasifier and the combustor is carried out effectively. The gasifier must be operated under pressure, and this introduces the problem of pressurized fuel feeding. Thus, additional investment in auxiliary units is inevitable with the resulting increase in investment and maintenance costs. The high-tech equipment would require services of highly skilled personnel to operate and maintain. As such it is not suitable for application as a village size power plant.

So far, the technology for hot gas cleaning has not been made any cheaper given the known problems with alkali metals and ash particles [47]. An investigation of the gasification process was made in order to identify and to propose feasible approaches in the biomass gasification process for gas turbine applications. An EFGT system, with the scheme shown in Figure 14, is designed to overcome the challenges of deposition and corrosion in the gas turbine unit.

Figure 13: Directly fired GT scheme

The application work best with the updraft gasifiers where thermal efficiencies and internal gas filtering mechanisms are better when compared to downdraft gasifiers. More interest has developed into studying and developing the EFGT system fired with gasified biomass fuels because it uses a relatively clean air to drive the gas turbine [26] [49] [50].

Figure 14: EFGT system Scheme

The critical component in the EFGT system is the heat exchanger whose design and operating performance affects the overall system efficiency [51] [43]. Deposition problems, which are known to occur in the turbine units when producer gas from biomass are used in directly fired GT systen, are expected to occur in the heat exchanger component. It is not yet known whether that change in the system design would instead lead to frequent maintenance in the heat exchanger component for small scale applications in the capacity range below 300kWt. There is need, therefore, to ascertain the extent of alkalis carryover in the producer gas stream so that some optimization method is identified in the gasification process to minimize the effects of corrosion and deposition in the heat exchanger unit.

With the introduction of the heated compressed air as the working fluid, the EFGT system efficiency is greatly dependent on the hot air temperature into the turbine inlet which is dependent on the heat exchanger material operating temperature [26]. The producer gas combustion temperature is about 1200oC while an alloyed steel (such as Allegheny Ludlum A286 Iron-Base Super alloy - UNS S66286) material has continuous maximum operating temperature of about 850oC. At about 1200oC this material cannot support the operation due to large thermal stresses which would develop, therefore some form of cooling of the combustion gases before transmission through the heat exchanger is inevitable. The cooling is achieved by dilution of the combustion products with air from the compressor like always used in gas turbines. This leads to exergy losses but not any energy losses. The cooling subsequently reduces the overall system efficiency since the efficiency depends also on the turbine inlet temperature.

2.6 Conclusions and Recommendations

Biomass gasification technology has been successfully demonstrated in large scale power generation and heating plants [19], but they are still considered expensive in comparison to fossil fuel based systems and therefore face economical, technical and other non-technical barriers while trying to penetrate the energy markets. This impediment can be overridden by carefully considering the gasification technology improvement strategies and recommending designs that are easier to construct, operate and maintain, suitable for rural Africa. Careful consideration need to be taken when venturing into commercialization of biomass gasification technology due to the many factors that influence its performances.

The challenges experienced with biomass fuel gasification necessitated an investigation into analyzing the technical problems associated with the application with IC engines. Experiments were carried out with biomass fuels in downdraft and updraft gasifiers to determine their technical performances. This report present some of the findings presented in line with the aforementioned objectives. And the following outline concludes the introductory part of this work.

- There is availability of un tapped biomass resources in Uganda which can be used for energy production

- Biomass gasification technology integration with IC engines and gas GT systems can provide an alternative for power generation in rural villages of Uganda. But there are concerns that need to be addressed among which are: gas cleaning methods, competition from fossil fuel systems, convenience of operation, decreased reliability of the equipment after extended operation.

- Application of producer gas from biomass gasification processes in IC engines is a viable approach, but gas cleaning for abrasive particles and tar create some challenges.

- Tar cleaning techniques being tested in demonstrations plants in Europe are very costly to be employed in biomass gasification plants in rural villages of Africa.

- Producer gas tar cleaning methods employed in developing countries raises some concern on the adequacy of the treatment methods used on the tar contaminated water.

- Hot producer gas from biomass gasification process applications with GT systems experiences problem of hot corrosion, erosion and clogging. These detrimental effects can be avoided by use of EFGT system.

• Details about EFGT system heat exchanger performance when used as air heating medium with hot combustion products of producer gas combustion is not known and require some studies. Some of these issues will be covered by the present study.

3. Design Considerations for an Externally Fired Micro Gas Turbine (EFGT) Heat Exchanger Using Biomass as

Fuel

- Introduction

The use of biomass as a primary energy source for electricity generation in small scale (below 1 MW electric) includes many challenges as noted earlier. Gasifying the biomass and using the producer gas as fuel in an internal IC engine driving an electric generator is one possible process, but experience has shown that operational problems caused by tar in the gas increase with the increase in system size. It was therefore interesting to explore another biomass fuel conversion process for applications with energy production systems.

The EFGT system is one alternative to IC engines for integration with biomass gasifiers, mentioned earlier. And for better performance realization, the heat exchanger surfaces used in the EFGT system must be able to operate at temperatures of about 30-50oC above the turbine inlet temperature (TIT) [52] . By the nature of the gas stream involved, deterioration in performance is a common occurrence when biomass fuels are utilized. The diminution in the heat transfer effectiveness and the corrosion of the material may be caused by ash, soot and alkali metal compounds carried in the hot gas stream generated from the gasified biomass. Alkali metals raise a serious concern, because they are the precursor to high temperature material deposition and clogging problems experienced with use of biomass fuels.

It is known that the product gas temperature from an updraft gasification process is lower than that of a down draft one [53]. Thus, it is anticipated that the carry-over of alkali metal compounds in the gas stream is low with the updraft gasification mode (see chapter 4 for a discussion on alkali metals). This was the motivation for the study of the updraft gasification process for integration with an EFGT system.

This chapter aims to present the relevant issues involved in designing one of the heat exchanger type for EFGT system application. A shell and tube heat exchanger was designed for an EFGT system consisting of a Rover IS/60 gas turbine. The uncertainty in determining the heat exchanger surface area as a result of variations in the input parameters was studied. Tests with a heat exchanger utilizing hot gas generated by combustion of producer gas from an up-draft gasifier shall be needed for assessment of operating potential at targeted TIT of about 1000 K.

- EFGT System Modeling and Simulation

3.2.1 Method and assumptions

The first step in analyzing the EFGT was to study the thermodynamics of the system illustrated in Figure 14, section 2.5.3. Known correlations and derived thermodynamic relations were compiled into a program on a computer to determine mass and energy balances for each of the components of the system. Temperatures, pressures and mass flow rates of the gas stream were determined at every mass entry and exit points for each component. Key assumptions included the following:

  - Ambient conditions assumed for the model runs were 25oC (298K) and 101.3 kPa

  - Thermodynamic properties taken from the air and gas property tables at the relevant temperatures and pressures.

  - Heat transfer coefficient determined as average for gas and air stream at inlet and outlet conditions.

  - An average moisture content of 20% for the raw biomass fuel was used, which provided a fuel with a heating value of 17 MJ/kg.

  - Heat exchanger effectiveness was assumed to be 0.85

  - Ideal gas behavior was assumed for the gas streams.

  - Total Pressure loss allowable in the system was 4% of the compressor output pressure.

Mass and energy balance for the gasifier and combustor units modeled were determined by taking a control volume approach, whereby the first law of thermodynamics and the law of conservation of mass and energy were applied to arrive at the final gas properties. Air mass flow rate of 0.612 kg/ s for the Rover IS/60 GT was used as input data for air flow quantity in the program. The airflow and the specified compressor isentropic efficiency of 78% were used as input into the program to determine the unknown compressor outlet temperature. The parameters that could be varied were turbine inlet and outlet temperatures, air mass flow rate, fuel consumption and pressure ratio.

Relations were then developed to depict the power output of the turbine over a range of conditions, which depended on the amount of biomass energy available and on the maximum TIT that could be achieved. These relations, together with the heat exchanger and turbine model were used to determine the pressure, temperature and mass flow rate at major locations in the modeled EFGT system.

3.3 Results and Discussion on EFGT Technical Performance

Figures 15a shows the variation of total system efficiency with pressure ratio at different values of TIT. Looking at the system performance, system efficiency depended on TIT. Lower values of pressure ratio at moderate TIT gave better efficiency. At 900 K the overall system efficiency was determined to be about 9%, and at 1000 K, about the maximum temperature for a low alloy steel heat exchanger, efficiency was about 13%. At 1300 K it was almost 21%, but at that temperature the system would require special alloy steel or ceramic heat exchangers. Optimum pressure ratio over the compressor was determined to be about 3.4. All these values are obtained without recuperation.

The variation of net power with pressure ratio for different values of TIT is shown in Figure 15b where net power was found to be depended on both pressure ratio and TIT. Lower temperature resulted into low power output just like in a conventional GT. In this case the maximum net power output for a given TIT was represented by pressure in the range of 3.0- 4.5 bar. Therefore, the EFGT system would be operated at low pressure ratio for a desired TIT in order to realize

good performance.

(a)

It is evident that the plant efficiency is strongly dependent on the hot air inlet temperature to the turbine unit. In practice, the turbine inlet temperature will be limited by the maximum operating temperature of the heat exchanger material. Creep failure is the most likely mode of failure under thermal and mechanical stresses, while high temperature corrosion would result from chemical reactions in deposits on heat transfer surfaces. According to one manufacturer of the heat exchanger tubes whose properties were used in this study, the maximum possible temperature of the gas stream entering the heat exchanger is limited to 8150C (1088K). This translates to a TIT of about 1000K and efficiency of about 13% at a pressure ratio of 3.5. The limiting temperature value was chosen for a material of high temperature operating condition specified as Allegheny Ludlum alloy -AL 800 of stainless steel series.

Variation of System Efficiency with Pressure Ratio for Different TIT 120 F 1 1 1 1 1 1 1 1 1 1 1 :

2 3 4 5 6 7

Pressure Ratio

2 3 4 5 6 7 Presure Ratio

(b)

Figure 15: (a) Variation of system efficiency with pressure ratios at different TIT and (b) Vartiation of Net power output with presure ratio for different TIT

Higher efficiency can be obtained with ceramic heat exchangers and such designs have been tested in other applications, so far the experiences are discouraging. Trials with ceramic materials for heat exchangers construction have shown that brittleness of the ceramics is the leading problem when combining with metallic materials in the design. Further work is being done to develop the heat exchanger materials to meet both operation and cost requirements.

3.4 Heat Exchanger Design Considerations

From the simulations done and other related studies, it was shown that the main drawback of external firing approach compared to the conventional cycle utilizing fossil fuel is the low efficiency when a high temperature heat exchanger is not used [26] . Due to the constraints imposed by low metallic heat exchanger maximum operating temperature, the TIT is much lower than that of the conventional cycle or ordinary turbine engine [51] [54]. The immediate remedy to low temperature problem associated with use of metallic heat exchangers can be overcome by the utilization of ceramic based heat exchangers, which are currently being developed although the

cost involved is quite unfavorable at the moment. The heat exchanger design, therefore, involve challenges related to; the high operating temperatures, pressure losses and fouling on the heat transfer surfaces. Currently, there are no off-the-shelves heat exchangers designed for service conditions that can be adopted in the EFGT system, especially for application with biomass fuels through a gasification process. The operating condition requires a high temperature material, which can withstand continuous operation above 850oC and easy to service. In light of the maintenance concern, the shell and tube heat exchanger was found suitable for this application. The tubes can be designed with single passes that can allow for easy cleaning by mechanical means (manually).

According to Mueller [55], the gas stream in the tube of a shell-and-tube heat exchanger should be selected, in this case, as one having more fouling tendency, which was the criteria utilized in this work. Single tube pass design was considered for passage of hot gas stream for the purpose of easy cleaning, and TEMA type E shell was selected with baffles to approximate a counter flow pattern. The design was carried out using ASME Boiler and Pressure Vessel Code, Section VIII and TEMA codes, which are accepted codes used in the USA and many other developed nations. Thermal design analysis resulted into a surface area with a safety factor of 1.1, and the result of thermal design calculations is shown in Table 8.

3.5 Consideration of Uncertainty in the Heat Exchanger Design

In the thermal design of a heat exchanger, parameters used to arrive at a required size of the exchanger are derived from physical properties such as; thermal conductivity, density of fluid stream, viscosity and specific heat.

These parameters are not exactly known; therefore, they are taken at their mean values for the calculations involved. It is apparent that the choices of mean values for properties and dimensions carry with it the inherent uncertainties in the quantities which they represent, as functions. Some of the examples include pipe dimensions not being uniform, fouling factors of the fluid stream cannot be measured exactly, and values for heat transfer coefficient are spread about the mean. It was noted that the important unknowns in the design of a single phase gas heat exchanger are:

- The nature and degree of fouling

- Local heat transfer variations in the heat exchanger

- The exact fluid stream flow and velocities on the shell side

Most design methods available in literature have assumptions such as constant parameter values for shell-side and tube-side, taking shell-side cross flow area at the center, and properties of fluid taken at the average temperatures. More of this is discussed by Frank [56]. Considerations of these assumptions paved way for safety factor inclusion to allow for uncertainties in the heat transfer equations that are normally up to 20-30 % in the best of the design methods as mentioned by Gupta [571.

Table 8 : Heat Exchanger Specification Sheet

| Service of Unit: Heating of Air by hot gas ; | Size: 488kWt |  | Type: BEP | Connection Type: None |
| --- | --- | --- | --- | --- |
| Performance of one Unit |
| Fluid Location | Shell Side | Tube side |
| Fluid Name | Air | Flue Gas |
| Fluid Quantity, Total [kg/s] | 0.612 | 0.74 |
| Vapor |  |  |
| Liquid |  |  |
| Steam |  |  |
| Water |  |  |
| Non condensing |  |  |
| Temperature (In/Out) [K] | In-500 | Out-973 | In- | 0ut-600 |
| Specific Gravity | 1.452 | 0.34 |
| Viscosity, Liquid |  |  |
| Molecular Weight, Vapor |  |  |
| Molecular Weight, Non condensable |  |  |
| Specific Heat [kJ/kgK] | 1.061 | 1.099 |
| Thermal Conductivity [w/mK] | 0.04939 | 0.05716 |
| Latent Heat |  |  |
| Inlet Pressure [kPa] | 356 | 102 |
| Velocity [m/ s] | 15.23 | 12.68 |
| Pressure Drop Allowable. Calc.[%] | 4 |  |
| Fouling resistance (min) | 1/100000 | 1/10000 |
| Heat Exchanged [kW] 488 |  |  | MTD(Corrected) 178 [K] |  |  |
| Transfer Rate. Service |  |  |  | Clean |  |  |  |  |
| Construction of One Shell | Sketch of Bundle Orientation |
|  | Shell side | Tube side |  |
| Design/Test Pressure |  |  | 105 | 455 |  |
| Design Temperature |  |  | 1000 | 1200 |  |  |  |  |
| No. Passes Per shell |  |  | 1 | 1 |  |  |  |  |
| Corrosion Allowance |  |  | 3 | 1 |  | KJ | o |  |
| Conn ection Size and |  |  |  |  |  |  |  |  |
| Rube No. 32; OD: 25.4 [mm]; Thickness 2.7 [mm]; Length 2 [m]; Pitch 32 [mm] In. 30 degrees |
| Tube Type: Plain; Material: Allegheny Ludium AL 800 stainless steel series |
| Shell ID: 524 [mm] |  | OD: 536 [mm] |  | Shell Cover |  |  |
| Channel of Bonnet: Channel | Channel Cover |  |  |
| Tubesheet Not Stationary | Rubesheet Floating |  |  |
| Floating Heat Cover |  |  | Outside packed |  | Impingement |  |  |
| Baffle-Cross Type: Single Segement; % Cut(Diam/Area) 25; Spacing: c/c[mm] 158; Inlet uniform |
| Baffle-Long |  |  | Seal Type- |  |  |  |  |
| Support Tubes U-Bend | Typ |  |  |  |  |  |  |
| Bypass Seal Arrangement | - Tube-Sheet joint welded |  |  |  |  |  |
| Expansion Joint- None |  | Type: |  |  |  |  |  |
| Pv2 Inlet Nozzle |  |  | Bundle Entrance [kPa] 3.24]; Bundle Exit:[kPa] |  |  |
| Gasket- Shell side |

These are quite conservative safety factors which could increase the cost of equipment considerably. The need to have a safety factor is critical, but the justification requires careful scrutiny in order to avoid over design on the other hand. Therefore, to be certain of the safety factor in a design of a heat exchanger one poses the question: what is the optimum surface area that would allow for the realization of the required TIT? There is attempt to answer this question in the following paragraphs.

In order to understand the effect of uncertainties on the design, attention was drawn on to analyzing an already designed heat exchanger with clear specifications ready for manufacture, refer to Table 8. Because an already designed heat exchanger was sized with mean values of design parameters, the probability that the equipment will meet its design thermal load requirements is 50% as observed by Cho [58]. In order to realize a good design, it was necessary, therefore to consider uncertainty analysis for all major design parameters. The most representative of these parameters in the determination of the exchanger surface area are the heat transfer coefficient values and the fouling factors of fluid streams involved. Assuming that all parameters fall within error limits following a normal distribution, sometimes referred to as Gaussian distribution, the degree of data spread around the mean value can be quantified using the concept of standard deviation. To obtain a normal distribution a recorded occurrence of an event many times is required, but in this case there was no such data to begin with. Therefore, a basis to build on was necessary so that a normal distribution could be realized from the available data. This then prompted the idea of Monte Carlo simulation method discussed in the next section.

3.6 Simulation to Determine Heat Exchanger Design Uncertainties

3.6.1 Monte Carlo simulation

A Monte Carlo method was used to carry out this simulation. The name Monte Carlo was coined by S. Ulam and Nicholas Metropolis in reference to the games of Chance, a popular attraction in Monte Carlo, Monaco [59]. One of the advantages of the method in simulating real systems is the ability to take into account randomness, by investigating hundreds of thousands of different scenarios. The results are then compiled and used to make decisions.

A Monte Carlo method is a technique that involves using random numbers and probability to solve problems. In this simulation method, the random selection process is repeated many times to create multiple scenarios. Each time a value is randomly selected, it forms one possible scenario and solution to the problem. Together, these scenarios give a range of possible solutions, some are more probable, others less. These values are taken from within a fixed range and selected to fit a probability distribution like the Gauss distribution curve, commonly referred to as the bell shape curve. The outcome is always within a specified range and there is an equal opportunity for any number to be the outcome within the specified range. The maximum and minimum values are obtained from known real occurrences of deviations of parameters within a certain limit. The accuracy of this method can be improved by simulating more scenarios. In fact, the accuracy of a Monte Carlo simulation is proportional to the square root of the number of scenarios used. This method is advantageous because it is a direct application approach that is able to solve a problem for which no other solution methods exist.

Computer simulation was carried out with a model to imitate a real life scenario and to make predictions on anticipated events. The model was created in Microsoft Excel windows application, and a certain number of input variables i.e. heat transfer coefficient, fouling factor and tube thickness values were employed in the model which gave a set of outputs. This model was deterministic. The program could iteratively evaluate the deterministic model using sets of random numbers as inputs which resulted into a creation of a stochastic model.

3.6.2 Application of Monte Carlo

Multiple trials were implemented by propagating a basic formula as many times as the number of iterations required for better approximation of the real situation could be used. Consider the parameters expressed in Equation 1; each parameter had a value contained between the maximum and minimum values as specified by their individual error limits. In other words, the fluid stream properties were defined at inlet and outlet temperatures within their error limits. Each of those parameters had a unique distribution and it was assume acceptable to have a uniform distribution without compromising the results. The imperative assumption was that parameters were mutually exclusive, which implied that variations in one did not influence another.

1

Urnf =		[Equation 1]

^cof ((1/ho) + Rfo + (w / kw )(Ao / Am) + (Rfi + (1/hi (Ao / Ai.))	[ q	]

[Equation 1]

Where:

heat transfer coefficient Rfo , fouling resistance on the outside of the tube surface

ho , heat transfer coefficient on the outside of the tube surface hi , heat transfer coefficient on the inside of the tube surface w, tube wall thickness Ao tube outside surface area

tTL(Do - Dt)

Am, arithmetic mean of surface area defined as 			 with D0 and Dt being the tube

outside and inside diameters respectively

kw, thermal conductivity of the wall material

Rf, fouling resistance on the inside of the tube surface

Therefore, the total surface area was a random variable determined within the minimum and maximum values of the solutions generated. Since the exchanger surface area calculated formed a variable of random numbers, it was expected to be a normal distribution, which was the reason why individual distributions of each variable were not important. The input parameters were then; heat transfer coefficient of the fluid streams, fouling factors and the tube thickness. Table 9 gives the ranges for the parameters employed in the calculations.

Table 9: Some of the maximum and minimum values of parameters used in Monte Carlo Simulation

|  | Max. value | Min. Value |
| --- | --- | --- |
| Heat transfer coefficient gas [W/m2K] | 28.76 | 19.17 |
| Heat transfer coefficient air [W/m2K] | 58.28 | 38.85 |
| Tube thickness (t) [mm] | 2.64 | 3.45 |
| Fouling | 1/10000 | 1/100000 |

Heat transfer coefficient is dependent on the Reynolds number, Prandtl number and the thermal conductivity of the fluid stream involved. It varies with the given parameters according to the flow geometry and the temperature of the fluid stream. Therefore in determining its values there are uncertainties incurred inherited from the input parameters causing its value to vary over some average. Also the empirical correlations as such are associated with uncertainties. Here an error limit of 20% is used. The tube thickness limits were determined using the specified ASTM standard for tubes with thickness, t, expressed as 0.2tn < t < 0.125tn, where tn is the mean thickness. Fouling resistances were read from fouling resistance tables for air and flue gases.

At first the random values for each input were generated from the bounded values, and later the area required was calculated using the generated results. The resulting area was then the mean value of those area values for all the runs. As mentioned above, the task commenced by generating random values for each of the parameters within their error bounds, and assuming a uniform distribution, the RAN () function was used to generate random numbers in the interval (0, 1) and multiplied these by the range of each variable as presented in Equation 2. The range was defined as the difference between the maximum and minimum values. This is expressed below and it generates random numbers in between maximum and minimum values of the specified range.

RAN ( ) x (Maximum - Minimum) + Minimum	[Equation 2]

3.6.3 Determination of number of iterations

The Monte Carlo method provides an estimate of the expected value of a random variable and predicts the estimation error, which is inversely proportional to the square root of the number of iterations. The total error e is defined by using three standard deviations (36) expressed in the Equation 3. 3a

£ = .—	[Equation 3]

VN

Where, 6 is the standard deviation of the random variable estimated with upper bound and N as the number of iterations. This calculation of the standard deviation is carried out of the maximum, the minimum and average values of the random variables as expected value from the Microsoft Excel windows application spread sheet function STDEVP().

The expected surface area was calculated as the random variable average for the surface using the function AVERAGE () in excel spreadsheet. The 36 accounts for the 99.7% of the sample population being studied in this case for a normal distribution.

The limits for the physical parameters such as tubes internal diameters were taken from the ASTM specified variations, temperature variations where determined through calculations using Logarithm Mean temperature. The mean and standard deviations for the surface area were determined for 10000 runs.

3.7 Discussion on Uncertainty Analysis Results

Turbine inlet temperature, TIT, depends on the amount of heat transferred to the compressed air flowing to the turbine. This is dependent on the heat exchanger tubes total surface area , which is first determined using the sizing method. The expression for relation between TIT and total exchanger surface area is shown in Equation 4 below.

20 A

Where, Q is the heat load and A is the total exchanger surface area.

Figure 16 shows the simplified spread of surface area about Amenn with standard deviation, ±o. In the decision-making on the acceptable TIT for better performance, it is justifiable to consider values from Ammn toward the right of the curve so that TIT is not below the desired value to cause under design problem.

Figure 16: Normal distribution curve

The significance of this analysis is to ensure that the exchanger surface is not over-designed or under-designed.

TIT - TgaS_ in	7 + Tgas_ out ~ Tair_ in	[Equation 4]

The plot in Figure 17 represents the frequency distribution curve that was generated using the Monte Carlo simulation approach. It is therefore certain that the surface area approximate a normal distribution curve and this could be a much smoother curve if many more simulations were to be carried out.

The mean of surface area gave an error limit of 15.51%, which can be interpreted as the safety factor equivalent to 1.155. The surface area determined by analytical method was 49m2 and that obtained by using simulation method gave approximately 54 m2. These two values had a difference of about 5m2 which is 9.3% variation. The difference between analytical and simulated results can be attributed to the use of average values of parameters at inlet and outlet conditions. It is most likely that the average values of heat transfer coefficient were overestimated in the analytical method, which resulted into a small exchanger surface area. Simulation offered a better result considering the common practice where safety is a major indicator in determining a heat exchanger surface area.

Therefore, the 15.5% error on the surface area seem to indicate that the 20-30% factors commonly employed in practice, which looks very conservative, can be acceptable to cover up for the uncertainties of the fluid streams properties. It is desirable to maintain the exchanger surface area to about and above the mean values determined so that the TIT is maintained at the desired level for better performance of the turbine system.

3.8 Conclusions and Recommendation

- In the EFGT system, the heat exchanger is the critical component whose performance affects the whole system efficiency.

- Optimal performance of the EFGT system can be achieved at low air pressure ratio of about 3.4 and at moderate TIT of about 1000K.

- TIT depends on the heat exchanger effectiveness, which also depends on the maximum allowable heat exchanger material operating temperature in the EFGT system. TIT determines the EFGT system efficiency.

- In the design of shell and tube heat exchanger for EFGT system, design factor of over 1.2 is sufficient to employ.

- There is need for further studies on the fouling levels in the EFGT system heat exchanger unit, especially due to alkali metal compound deposition.

4. Alkali Metal Compounds Retention in an Updraft

Gasifier

4.1 Introduction

There is a growing interest in biomass gasification application with gas turbine (GT) mostly for small scale power plants. GT systems present great potential in the biomass gasification industry where small scale applications with steam turbines are not economically viable [60]. However, there are challenges met when operating GT with product gas from biomass gasification. One major challenge in the application of biomass fuel relates to the product gas quality. The generated gas requires proper treatment to avoid deleterious effects it can cause in ferrous materials for high temperature applications. With careful consideration, the GT industry developed criteria for product gas quality for applications with GT. The meeting of the criteria is significant to achieving effective operations with biomass fuels in GT.

The goal of biomass gasification is to obtain a combustible product gas, but many undesirable constituents are formed in the process. Of particular interest in this study are the alkali metals, which occur naturally in raw biomass fuel as free elements and as complex compounds. These alkalis in their various forms are vaporized during a thermal gasification process and their vapors react to form inorganic compounds of salts and oxides. The alkali may bind with one or more of the following elements: calcium, chlorine and sulfur (Ca, Cl and S). Entrainment of some of the new compounds formed in the generated product gas stream is very detrimental to the service life of the downstream equipment. Studies have shown that the alkalis are in vapor state at temperatures above 800oC in the biomass gasification process [611, [39]. The most problematic are K and Na salts. Their quantity in the gas phase in an updraft gasifier is not known, and whether some proportion are entrapped in the fuel bed and later transported to the ash bed there is no literature available.

The objective of this study was to establish the extent of the alkalis retention in an updraft gasifier intended for application with the EFGT system. In the EFGT system a heat exchanger medium is integrated to obviate the direct use of adulterated producer gas in the GT, see section 2.5.3 for details and the work of Kautz and Hansen [62] for further discussions on EFGT system.

An updraft gasifier was chosen for this study because of the relatively high calorific value gas it produce, better thermal efficiency, and for the alkali metals retention potential anticipated, among others. Experiments were carried out to generate product gas with the fuel feed and airflow rates chosen to resemble those used in an experiment by Di Blasi et al [63] to allow some comparisons with a bench scale gasification experiment. The gases realized were analyzed for contents of alkali metals and gas composition.

4.2 Experiments

In this investigation, two raw fuel samples, 8 mm diameter, 5-15mm long, from pellets of softwood shavings and reed canary grass, all of commercial qualities were used. Experiments were carried out in an updraft gasifier where the generated producer gas was analyzed online to determine the gas composition. Sampling for the alkali metals in the gas phase was also carried out at the same time.

4.2.1 Equipment description

A 17kWt updraft gasifier constructed from a stainless steel pipe of internal diameter 165mm and standing 1250mm high above the grate was used. Temperature probes were installed through the gasifier top plate along the gasifier central axis and near the wall. A gas sampling pipe and bed height probe were included in the construction. The inclusion of a fuel bed height measuring probe allowed monitoring of the bed height. A detachable ash pot placed in a water jacket was installed below the grate. The grate consisted of 10x5mm square mesh grids. Figure 18 was photographed after the first experiment with wood pellets, and the grey and black spots within the mesh are ash and char residues. The complete gasifier measurement equipment are presented in Figures 19a and b.

The screw fuel feeder used was calibrated to allow for steady bed height in during the experimentation process. It was was connected in series with a motorized ball-valve with one end of the recess sealed to form a small feeding cup (A model drawing shown in Figure 19c). The cup feeding mechanism diminished gas leakage into the laboratory hall greatly. Supply lines from compressed air and nitrogen tanks in a nearby paper-mill factory delivered these gases to the gasifier through a computer controlled gas flow regulators. Nitrogen was used for leak checks and extinguishing the combustion process during normal shutdown.

Figure 19: Gasifier details: (a) construction dimensions in mm, (b) Connections of components, and (c) motorized half-closed ball valve model

(a)

(c)

4.2.2 Experimental method

Wood pellets feeding rates in the two experiments carried out were 3.4 and 3.6 kg/h at the given air flow rate of 4.3 kg/h (60NL/min). A similar airflow rate was used with reed canary grass pellets, but at a feed rate of 4.1kg/h. The stoichiometric air-fuel ratios therefore were about 0.215 and 0.210 for wood and reed canary grass, respectively. Both fuels presented grate loads of about 800kW/m2. The bed height probe was used to monitor the height of fuel bed, which was maintained in the range of about 350-450mm above the grate in all the experiments.

Product gas mixed with methane was ignited in a simple gas combustor connected to the gasifier outlet. A self-sustaining flame from the product gas combustion was realized after the first 10 minutes of run. Steady conditions were determined by the stabilization of the temperature values being read from all thermocouples installed in the gasifier. Temperature values were recorded and stored on a computer, and product gas composition was analyzed every 5 minutes and values were recorded on a separate computer throughout the experiment.

4.2.3 Measurement technique and sampling methods

In order to understand the condition and behavior of our equipment, preliminary test runs were conducted. This was to determine the necessary time needed to achieve stable temperature conditions within the gasifier before sampling for the alkali metals could commence. Checks for leakages in the system were done using an online Micro GC connected after the filters. Zero sample analysis for the test Teflon filters was carried out using Inductively Coupled Plasma Atomic Emission Spectroscopy/ Mass Spectroscopy (ICP-AES/MS). This was to determine the inorganic element content and to identify the measurement method to employ. The analysis results turned out that less than 1% of the filter content consisted of inorganic elements of interest to this study. Therefore the content was within the recommended limit for applications with filtration methods used in sampling of the alkali metals.

The Micro-GC was used online for gas analysis of samples drawn through the filters for quantities of CO, CO2, H2, CH4, C2H2, C2H 4, C2H6, N2 and O2. The constituent quantities were compared to that obtained with the gas drawn without passing through the filters in order to identify any leakage that may arise in the system. Temperature measurements were made at 9 points along the central axis and near the wall inside the gasifier.

Temperature values read through an analogue digital converter were recorded on a computer. After two hours of run, the filter holders with Teflon filters inside were first heated to about 220oC and at that temperature the producer gas was drawn using suction pump through the filters to collect samples for about 50 minutes during sampling. This time allowed for isokinetic total dust sampling in 1nm3 of gas drawn as required by the Standard BS EN13284-1 with the exception, in this case that a 10 micron particles size limiting cyclone was connected upstream the filter holder.

In the second experiment with wood pellets the producer gas drawn through the filters was bubbled in distilled water as sorbent for alkali metal compounds in a gas wash bottle. The alkali metal compounds that might have passed through the filters were finally retained in the water. Earlier a zero analysis was carried out on the distilled water to ensure no appreciable amount of the alkalis were present to interfere with sample integrity. The total concentration of K, Na, Ca, Cl, S, Pb and V were determined from samples collected by total dust sampling and absorption in gas wash bottles. The analyses of the dissolved elements were determined using X-ray Diffraction (XRD) and Inductively Coupled Plasma Atomic Emission Spectroscopy/ Mass Spectroscopy ICP-AES/MS methods. At the close of each experiment the gasification reaction was extinguished using nitrogen gas. The retained char in the bed, un-burnt wall residues and ash on grate and in the ash pot were analyzed. Quantitative analyses of the ash content for the

experiments were carried out to determine the quantities of different constituents of the ash.

4.3 Results and Discussion

4.3.1 Ultimate analysis

Test results carried out on raw fuel samples of wood and reed canary grass pellets are presented in Table 10. It is evident from the results that reed canary grass pellets have relatively high quantities of K, Na, Ca, Al, Cl, S, Si and ash compared to wood pellets. These elements are considered most important in the release of inorganic compounds in a biomass thermal decomposition. The proportion of Na compared to that of K and the other elements in both fuel samples was lower.

Table 10: Raw fuel composition including main ash-forming elements of the used pellet fuels

|  | Reed canary grass | Stem wood-pine (planar shavings) |  | Reed canary grass | Stem wood-pine (planar shavings) |
| --- | --- | --- | --- | --- | --- |
| Dry substance | 89 | 92 | Asc | <0.3 | <0.1 |
| Asha | 7.4 | 0.3 | Bac | 15.7 | 7.78 |
| Cal. HHVb | 18.6 | 20.3 | Bec | <0.04 | <0.002 |
| Ca | 46.2 | 51.9 | Cdc | 0.0611 | 0.0301 |
| Ha | 5.7 | 6.0 | Coc | 0.25 | 0.0387 |
| Oa | 39.8 | 41.8 | Crc | 1.67 | 0.195 |
| Na | 0.9 | <0.1 | Cuc | 8.27 | 0.732 |
| Sc | 1330 | 57.1 | Hgc | <0.02 | <0.01 |
| Cla | 0.06 | <0.01 | Moc | 0.578 | <0.02 |
| Ala | 0.0465 | 0.00275 | Nic | 1.18 | <0.06 |
| Fea | 0.0362 | 0.00175 | Pbc | 0.929 | 0.0716 |
| Caa | 0.232 | 0.0682 | Scc | <0.09 | <0.004 |
| Mg» | 0.0730 | 0.00874 | Snc | <0.03 | <0.03 |
| Mna | 0.0163 | 0.00674 | Src | 10.5 | 4.45 |
| Pa | 0.110 | 0.00205 | Vc | 0.735 | 0.0136 |
| Naa | 0.0154 | 0.00134 | Wc | <4 | <0.2 |
| Ka | 0.256 | 0.0344 | Yc | 0.262 | <0.008 |
|  |  |  | Znc | 46.2 | 12.5 |
|  |  |  | Zrc | 1.9 | 0.0796 |

"Dry basis, wt-%;b Wet basis, MJ/ kg; c wt-% of sample

4.3.2 Temperature profiles

Temperature-time plots obtained with wood pellets gasification as measured by K-type thermocouples at different heights above the grate are shown in Figures 20 through 24. At the start of the experiments temperature variations were fluctuating greatly, which could be attributed to the dynamics of the fuel bed at startup. This fluctuation tendency was more pronounced in the bed from about 160 to 380mm height above the grate. Comparative steady state conditions were reached after about 200 minutes of run. Temperature profiles showed similarities to another study carried out with beech wood pellets where temperatures within the fuel bed ranged from about 1300oC to 500oC at 10mm to 280mm above the grate, respectively [63]. Temperature values read just above the grate and within the fuel bed were below the 700oC value for holding the alkalis in vapor phase [64]. This would suggest that the alkalis were contained generally within the

fuel bed and on the wall of the gasifier.

By comparing temperature values plotted in Figures 20 and 21, it can be noted that higher values were recorded for thermocouples near the wall than at the gasifier central axis. This was true for values read at corresponding heights above the grate. These deviations can be attributed partly to the differences between the thermal conductivities of the materials involved in heat transfer in the gasifier.

The gasifier wall, made of stainless steel material, had a higher thermal conductivity compared to the fuel bed material mixed with hot gas stream. The high thermal conductivity of the wall permitted quick heat conduction in the wall as compared to the majorly convective heat transfer phenomenon within the fuel bed. The heavily insulated heated wall radiated heat to the gasifier interior. Both occurrences allowed for higher temperature near the wall than at the center of the gasifier as compared away from the grate.

Experiments with reed canary grass pellets carried out in a similar manner gave temperature readings as shown in Figures 23 and 24. After the first 50 minutes of run serious fluctuations in temperature readings were noted especially within the fuel bed up to about 160mm height above the grate, which represented the pyrolysis zone. After 200 minutes of run, temperatures increased causing thermocouples burn-out for those within the 280mm bed height. Temperatures about type-k thermocouple range (1350oC) of operation were registered which could be attributed to slagging problems in the fuel bed as a result of ash melting. It was not possible to obtain any meaningful values for the temperature readings with reed canary grass fuel. This behavior relates to a study carried out with straw pellets in an updraft gasifier of similar size where, for two experiments with each having three hours of run, no stabilization in the temperature readings were realized [63].

1600 1400

<3200 !l000

■£800

CD

&600 E

^400 200

z=10mm

z=35mm

z=50mm

z=100mm

z=160mm

z=280mm

z=380mm

z=500mm

z=710mm

Hrwwvi =

WMitm mmm:.

0

ikmmammanm*i

0 67 133 200 267 333 400 467 533 600 667 733 Time in Minutes

Figure 20: Temperature time plot at different heights (z) along the gasifier central axis for first wood pellets experiment 1

z=10mm

z=35mm

z=50mm

z=100mm

z=160mm

z=280mm

z=380mm

1400

0 67 133 200 267 333 400 467 533 600 667 733 Time in Minutes

z=500mm

z=710mm

Figure 21: Temperature time plot at different heights (z) near the gasifier wall for first wood pellets experiment 1

Figure 22: Time temperature profile at different heights (z) along gasifier central axis for wood pellets experiment 2

Figure 23: Temperature -time plot at different heights (z) along the gasifier central axis for first reed canary grass experiment

Figure 24: Temperature -time plot at different heights (z) near the wall in the fuel bed for first reed canary grass experiment

4.3.3 Gas composition

The compositions of producer gas obtained during experiments with wood pellets are presented in Figures 25 and 26. These values were obtained with samples collected when steady conditions were realized during the experiment i.e. after about 200 minutes of run.

0

700

35

|  |  | ID □ |  |
| --- | --- | --- | --- |
|  |  | □ |  |
| D □ □ □ □ | □ □ □ □ □ |  |  |
|  | ■ ■ -V ■ |  |  |
| ■ A A A *** | 1 | ■ | / |

30

£ 25

20

8 15

o" o

cm" 10

100

200

300	400

Time (min)

500

600

& H2 a CH4 □ CO ■ CO2

5

0

Figure 25: Gas composition from wood pellets experiment

|  |  |  | □ |
| --- | --- | --- | --- |
|  | □ □ | □ g a a □ □ ° □□ m | □ t |
| ■ □ a □ ■ | □ □ - B □ ■ ■ | □ □ □ □ □ cp □ | □ □ □ □ oB a 1 \ |
|  | ■ | - lA | A^ A |
| A A | V |  | A |
| A * | > |  | JjA* A . 1 |

30

E 25

15

Si 10

100

200

300

400 500 Time (min)

600

700

800

a H2 □ CO a CH4 ■ CO2

5

0

35

~ 20 X

o

o

0

900

Figure 26: Gas composition from wood pellets experiment 2

In the first experiment, gas composition from wood pellets was 10-25% CO, 5-10% H2, 1-3% CH4, 7-14% CO2, and of C2H2, C2H4 and C2H6 below 0.5%. The second wood pellets experiment saw a higher calorific value gas with composition of 27-30% CO, 5-8% H2 and 2-3% CH4 and 4-7% CO2, obtained between 500-600minutes of run. Given the consistency in the

producer gas composition from the second wood pellets experiment, it can be concluded that wood pellets gasification reaction remained stable after the first 200 minutes of run. This also was one advantage in the sampling of the alkali metals, which allowed for a repeated sampling under similar operating conditions.

35

The composition of the gas obtained with reed canary grass pellets are presented in Figure 27. Considering the first 200 minutes of run, only CO at about 26-30% had composition similar to that of wood pellets experiment, but the rest (5-7% H2, 1-2% CH4, 4-5% CO2) showed no similarity at all. This can be attributed to the unstable gasification reaction occurrence with reed canary grass pellets where ash slagging interrupted the gasification process.

1.5

30

Shm

dP

□ Dp □

ntf?3 m a-- ID-

<g 25

a H2 □ CO a CH4 ■ CO2 o C2H4 • C2H6

o

° %

£ 20

% a

1 15

Cvf O O

8 10

t X

0.5

■ *

■	■ A^yA

A

5

jM

0

0

200	300

0

100

400

500

Time (min)

Figure 27: Gas composition from reed canary grass gasification experiment 1

4.3.4 Particulates analysis

The cooling of the gasifier using N2 preserved ash and char residues within the gasifier through its quenching action. Residues recovered in the process were; gasifier wall deposits, fuel bed residues, ash and char on the grate and in the ash pot. The char found in the ash pot were those that fell through the grate after being reduced in size by the combustion process to become smaller than the grate recesses. The ash pot content was categorized by sieving and consisted of 3-7 % by weight of particles with sizes less than 1mm. Since the temperature profiles within the fuel bed and the gas composition from the two wood pellets experiments were very similar after about 150 minutes from the start, this suggested that the gasification reaction and ash formation over the grate had reached a certain level of equilibrium. And is possible that this was the steady conditions attainable with these experiments for the given airflow and fuel feed height.

In the first experiment with reed canary grass, two thermocouples were burnt out within 180 minutes from the start and on continuation of the run temperature values could not stabilize but

kept on increasing. More thermocouples were lost together with their carrier tube which melted away, see Figure 28. In this experiment, the gasifier wall and fuel bed residues were recovered inform of char, ash and slag.

The second experiment with reed canary grass pellets was stopped after about 20 minutes from the start of the experiment when heavy gas leakage was realized from the gasifier side just above the grate. This hole was most likely created in the first experiment with reed canary by the high temperature ash melting process and the hole was hidden under the gasifier insulation. The high temperature within the bed above the grate effected the thermal corrosion of the gasifier wall. Therefore, test with reed canary pellets in the second experiment failed.

Figure 28: Photograph of thermocouple tubes showing parts of the normal and the melted tubes including thermocouple wires during the reed canary grass pellets gasification.

Table 11 show the analysis results of samples collected on Teflon filters from experiments with wood and reed canary grass. Concentration of K (94 ppbw) in the first sample taken 250 minutes from the start was almost double those of the proceeding samples. The 2nd and 3rd samples had very similar K concentrations of 50 and 60 ppbw of product gas respectively. High concentration results of the first sample could be the effect of unstable process startup in the fuel bed.

Analysis of filters from reed canary grass pellets however showed very significant deviations in K concentrations obtained from samples drawn after 150 and 400 minutes of run with 4.3 and 931 ppbw respectively. These values reflected the occurrence of higher temperatures of over 800oC within the fuel bed. The result was that larger concentrations of the alkalis were released from the fuel bed into the gas phase.

The second wood pellets experiment had also included sampling with gas wash bottles with details in Table 12. In this sampling, the elements Na, Ca, Cl, K, Pb, Mg, S and V were recovered from the gas drawn through the filters. It turned out that considerable levels of K and Pb concentrations were recovered in the gas wash bottle after the filters. Such levels of concentrations were unexpected after the filters, and one possible explanation could be attributed to tar as the transport medium for the species.

Table 11: K and Cl-content (re-calculated to concentrations in producer gas) in solid material trapped in the total particle filter ash during the initial experiments with wood and reed canary grass pellets, respectively.

| Experiment | First experiment with wood pellets | First experiment with Reed Canary Grass pellets |
| --- | --- | --- |
|  | K | Cl | K | Cl | K | Cl | K | Cl |
|  | (I g/nm3) | (□g/nm3) | (ppbw) | (ppbw) | (□g/nm3) | (I g/ nm3) | (ppb w) | (ppb w) |
| 1st sampling | Sampling time: 240-265 min after start | Sampling time: 130-160 min after start |
|  | 111 | < 301 | 93.7 | < 255 | 5.2 | 0 | 4.4 | 0 |
| 2nd sampling | Sampling time: 485-530 min after start | Sampling time: 395-420 min after start |
|  | 59.2 | < 187 | 50.2 | < 158 | 1099 | 252 | 931 | 214 |
| 3rd sampling | Sampling time: 700-750 min after start | n.a. |
|  |  |  |  | < 174 |  |  |  |  |
|  | 69.2 | < 205 | 58.7 |  | n.a. | n.a. | n.a. | n.a. |

In this experiment, filter holders were kept at about 220oC in order to avoid tar condensation and interfering with particulates filtration, but it is likely that the tar absorbed and transported some of the inorganic species across the filters, and to a greater extent, K and Pb were included among these elements. There was evidence of tar condensation downstream the filters as can be seen in Figure 29a. Figure 29b shows the section drawing of one side of filter holder.

| Rubber |  |  |
| --- | --- | --- |
| seal 1 |  |  |
| C^fl |  |  |
| Condensed | m ! |  |
| tars | /# | ■ |

Rubber senl

/GQS

Filter

gas outflow

(a)	(b)

Figure 29: Condensed tar after the filter in half of the filter housing (b) Filter holder simplified drawing

Table 12: K, Na, Pb, V, S, Cl, Ca and Mg content (re-calculated to concentrations in producer gas) in solid material trapped in the total particle filter ash and in the gas wash bottles during the second experiment with wood pellets.

|  | 1st sampling Sampling time: 180-220 min after start | 2nd sampling Sampling time: 510-560 min after start |
| --- | --- | --- |
|  | r g/nm3 | ppb (weight) | n g/nm3 | ppb (weight) |
|  | In/on filter | In gas wash bottles | In/on filter | In gas wash bottles | In/on filter | In gas wash bottles | In/on filter | In gas wash bottles |
| K | n.a. | 2821 | n.a. | 2391 | 33.9 | 1366 | 28.8 | 1158 |
| Na | n.a. | 156 | n.a. | 132 | 0 | 0 | 0 | 0 |
| Pb | n.a. | 95.1 | n.a. | 80.6 | 0.7 | 57.6 | 0.55 | 48.8 |
| Ca | n.a. | 269 | n.a. | 228 | 36.3 | 50 | 30.8 | 42 |
| Mg | n.a. | 7.8 | n.a. | 6.6 | 3.8 | 0 | 3.2 | 0 |
| S | n.a. | 3906 | n.a. | 3310 | 5.4 | 1159 | 4.6 | 982 |
| Cl | n.a. | 5902 | n.a. | 5002 | 0 | 2567 | 0 | 2175 |
| V | n.a. | 0.61 | n.a. | 0.52 | 0 | 0 | 0 | 0 |

The concentration of K at 1200ppbw in the product gas was way above the recommended levels acceptable in the gas for applications with LM250 gas turbine as shown in Table 13, and those for Pb, V and Ca were within the acceptable quantities [65]. It would be a strong reason for recommending the use of EFGT system so that the condensing of alkali metals in the turbine is minimized.

Table 13: Acceptable contaminant concentration in fuel for LM2500 gas turbine. Source: Nelson [65]

|  | Maximum concentrations in combusted mass flow to the turbine (ppbw) | Calculated maximum allowable concentrations in a typical biofuel (ppbw) |
| --- | --- | --- |
| Lead | 20 | 100 |
| Vanadium | 10 | 50 |
| Na + K + Li | 4 | 20 |
| Calcium | 40 | 200 |
| Sulfur |  |  |
| (Alkali metal sulfates) | 12 | 60 |

4.3.5 Alkali metals distributions

Elemental analyses were also carried out on the different samples taken from the wall, ash pot and on the grate. Results are presented in Table 14 for the second wood pellets experiment. K and Ca were the dominant alkali species in the analyzed samples. There is good consistency in the Ca/K ratio for all samples and for the fuel as well, which justifies to some extent the method employed for sampling and analysis.

The high concentrations realized of Fe, Ni and Cr can be attributed to their release from the scaling of the stainless still material from the gasifier wall. Their quantities therefore do not necessarily reflect those in the residues from the solid fuel.

Table 14: Elemental composition (main ash forming elements and some interesting trace elements) of the different solid residue samples produced in the second experiment with wood pellets

|  | Ash pot residue | Ash residue deposited | Wall |
| --- | --- | --- | --- |
|  | (char pellets+ ash) | directly above grate | residue |
| Dry | 99 | 99 | 80 |
| substansc |  |  |  |
| Ka | 0.77 | 10.54 | 0.10 |
| Naa | 0.045 | 0.32 | 0.0073 |
| Caa | 1.36 | 21.52 | 0.20 |
| Mgf | 0.16 | 2.62 | 0.02 |
| Fea | 1.01 | 5.52 | 0.82 |
| Ala | 0.05 | 0.79 | 0.01 |
| Pa | 0.08 | 1.07 | 0.04 |
| Sia | 0.42 | 4.51 | 0.19 |
| Cla | <0.1 | <0.1 | <0.1 |
| Sa | 0.02 | 0.24 | 0.02 |
| Znb | 7.47 | 27.3 | 212 |
| Pbb | < 1 | < 1 | 1.34 |
| Vb | 10.1 | 78.8 | 1.29 |
| Crb | 1040 | 13500 | 75.3 |
| Nib | 771 | 3610 | 1070 |

a) Dry basis, wt-% ,t) Dry basis, mg/ kg, c) wt-% of sample

Table 15 shows that no crystalline phases could be detected by XRD in the wall residue samples where the inorganic components of the residues were very low. Above the grate and in the ash pot Mg, CaO, K-Ca-carbonates and Ca-Mg-Silicates were dominating. K2Ca (CO3)2 was detected in the gas wash bottle samples.

Table 15: Phase identified (wt% of crystalline phase)* in the different solid residue samples produced in the second experiment with wood pellets.

| Compounds | Ash residue deposited directly above grate | Ash pot residue | Wall residue |
| --- | --- | --- | --- |
| MgO (Periclase) | 12 | 12 | „ |
| CaO (Lime) | 7 | 23 | -- |
| Ca(OH)2 (Slake lime) | 8 | -- | -- |
| CaCO3 (Calcite) | 2 | 18 | -- |
| K2Ca(CO3)2 (Fairchildite) | 10 | 15 | -- |
| CaMg(SiO3)2 (Diopside) | - | 8 | -- |
| Ca2SiO4 (Grammite) | 21 | -- | -- |
| Ca2MgSi2O7 ( Gehlenite ) | 8 | -- | -- |
| Ca3Mg(SiO4)2 (Merwinite) | 31 | 25 | -- |

* The proportions of the crystalline phases have been kind Determinedfrom semi-quantative Rieltveld analysis (TOPAS 2.1) of XRD data collected with DIFFRACplus [66]. Structural data from the ICSD for all phases served as models for the refinements [67]. The amorphous contribution to the diffraction pattern was treated as background and subtractedfrom the quantification.

The elemental composition of the residues are plotted in Figures 30 and 31 showing K and Na weight percentages as collected from different locations within the gasifier for the second wood pellets experiment.

50

K in producer gas K in ash residue on grate

K in ash pot K in wall residue K in other

fractions (e.g. char bed above grate)

45

5

0

Figure 30: Distribution of ingoing K (a) and Na (b) in the producer gas and the different solid residues fractions during the second experiment with wood pellets

40

"53

= 35 .c

5 30 *

CT

.EE 25 o

CT C

Z 20 o

115 10

50

45 40

a

■3 35 .c

a 30

E 25

o

ra

20

o

S 15 5

10 5

0

Na in producer Na in ash residue Na in ash pot Na in wall residue Na in other gas	on grate	fractions (e.g. char

bed above grate)

Figure 31: Distribution of ingoing K (a) and Na (b) in the producer gas and the different solid residues fractions during the second experiment with wood pellets

Table 16 presents quantities of the fuel consumed and the residues in the three tests carried out. The quantities were used in determining the alkali retained in the gasifier. The analysis from wall, ash pot and grate residues yielded, 3%, 32% and 42% respectively, implying a total of 77% of the K was retained in the ash. Similarly, Na content in the aforementioned sample order was 5%, 47% and 33% respectively, giving a total of 85% retention in the ash. The fraction distribution of sodium in the raw fuel samples are well below those of potassium as reflected in Table 14. The contribution of Na in the (K + Na) for wood fuel was about 4%.Thus the Na percentage in the raw fuel was very low, thus presents a very small fraction in the sampled residues rendering detection very difficult.

Table 16: Fuel consumption and residues obtained from the experiments

|  | Initial | Second | Initial experiment |
| --- | --- | --- | --- |
|  | experiment with | experiment with | with Reed canary |
|  | wood pellets | wood pellets | grass pellets |
| Duration of run [hours: minutes] | 13:46 | 9:34 | 8:19 |
| Total fuel feed [g] | 51812 | 32426 | 34413 |
| Wall residue [g] | 658 | 333 | -* |
| Fuel bed residue (char pellets) [g] | 1608 | 1707 | 2448 |
| Ash residue deposited directly above | 37.1 | 41 | -* |
| grate (ash) [g] |  |  |  |
| Ash pot residue (char pellets+ ash) [g] | 959.9 | 420.1 | -* |

Results from the wash bottle sample analysis yielded 1% of K from the product gas. Therefore, it can be estimated that 22 % of the K remained in the unconsumed char in the char bed which was not analyzed. When this quantity is added to that from ash analysis (77%), the result is 99% retention of the K in the gasifier. The major compound of K formed was K2Ca(CO3)2 which could only be detected by XRD. It can be speculated that K may exist in the ash in other amorphous form as slag such as in silicates with low melting temperature, but the amount of Si realized from ash analysis was lower than the K content. This would suggest that more of the K was available for bounding with other species forming compound of high melting temperatures than the silicates of K.

There were also a high proportion of Ca-Mg silicates detected in the different ash fractions. Through visual inspection, it was clear that there were no sintered materials in the ash pot and not even on the grate with the wood pellets experiments.

Therefore about 99% alkalis retention was possible in this experiment. Similar work conducted with small scale cyclone gasification of wood powder realized about 40-60% alkali retention [68]. Others; with fluidized bed biomass gasification attained values of 40-80% [69], another mentioned experiments with wood pellets (from pine wood) gasification at 1100-1200oC that yielded about 4% of alkali in the product gas and achieved 96% retention within the gasifier [70]. The retention level of alkalis in the updraft gasifier was found to be superior to those cited above.

The high alkali metal retention tendency of the updraft gasifier can be attributed to the cooling effects of the fuel bed. The hot gases are cooled while pyrolyzing and drying the fuel through the bed and the alkali metals are condensed on char particles which end up falling down through the grate to the ash pot Another explanation could be that the long residence time for the fuel in the bed would allow for formation of compounds such as K2Ca (CO3)2. In this case, silicates are not prominent since stem wood pellets were used with very low silica content due to generally less contamination with sand. Otherwise there would have been more silicates formation, had it been that the levels of silica were significant in the raw fuel.

4.4 Thermo-Chemical Modeling of Alkali Metal Compounds

Condensation Reaction in Higher Temperature Heat Exchanger

In order to understand the alkali metal compounds condensation reaction in a high temperature heat exchanger after product gas combustion, a computer based thermo-chemical model was used to simulate the situation. The condensation reaction was modeled with 2% excess air and this was used in the calculation and simulation of the condensation reaction phase status of the inorganic elements in the fine particles entrained in the product gas especially the K, Cl and S. Simulation was carried out for temperatures in the range of 400-1100oC at normal atmospheric pressure of 1bar in which the different phases of compounds formed from the three elements were studied. The temperature values represent the inlet and outlet temperatures in a high heat exchanger.

The computer program FACTSage 5.4 was used to model the condensation reactions and the calculations were based on the minimization of the Gibbs free energy for the components. The program retrieved data from its data bank built-in with thermodynamic data for a single gas including stoichiometric condensed phases, 2 non-ideal solutions of salt and oxide or slag, and 7 non-ideal solid solutions. The program then uses this information to determine the status of the different components as shown in Table 17. The input to the program was the concentrations of K, Cl, S and Ca obtained from the gasification experiment with wood pellets.

Table 17: Elements and solution models used in the chemical equilibrium model calculations 1 [73] .

Elements C, H, O, N, S, Cl, K, Ca

Solution models

Salt:

Chloride:

CO3SO4:

SLAGA (liquid) SALTA (liquid) ACL (solid solution) CSOB (solid solution) liq-K,Ca/CO3,SO4 (LCSO) s-K,Ca/CO3,SO4 (SCSO) liq-Ca,Mg,Na/ (SO4) (LSUL) s-Ca,Mg,Na/ (SO4) (SSUL)

4.4.1 Alkali compounds condensation reactions

The thermo-chemical reaction simulation results for the alkali metal compounds considered the four species i.e. K, Ca, Cl and S in the product gas after combustion. The results plotted in Figures 32 to 34 present prediction of what happens when temperatures in the range of 400- 1100oC, as expected in high temperature heat exchangers, is modeled

In Figure 32, analysis of K-species revealed that the species inform of K2SO4 condensate dominated after about 900oC and no chlorides of the alkali metal was formed after about 680oC since the preferential reaction yielded the sulfate component as long as the S-species was available to take up the K-species. Na was not included in the model because its concentration in the gas

1 The designations of the solution models are the ones used in FACTSage 5.4.1.

phase was very low and therefore with insignificant impact on the gas quality.

Sulfur is volatized to form the SO2 between 900-1100oC. The proportion of the oxide increases with temperature (Figure 32), and the oxide is understood to reacts with the K-species to form the K2SO4 at temperatures lower than 900oC. The hydroxide and chloride of potassium exists only up to about 700oC when the K-S reaction over takes them to form the solid compound- K2SO4.

On the other hand the dominant chloride compound formed below 700oC is HCl (Figure 34). It is known that chloride compounds have very high corrosion tendencies [62]' These simulation results show that product gas combustion applications through gasification have less chloride components in the condensed phase. This advantage is gained because of the higher S-Cl ratio, of which sulfur would dominate the reaction, creating non corrosive solid condensate of K2SO4. The Cl-species is then joined to the hydrogen and passed out as HCl in gaseous phase at the simulated outlet temperature of 400oC.

Temperature ( C)

o KOH (g) -a- KCl (g) -A- K2SO4 (g) * K2SO4 (s)

Figure 32:Chemical equilibrium diagram for cooling of the flue gases(produced by combustion of the wood pellet based producer gas in air to fuel ratio of 1.1) from 1100-400oC for the K-system.

o SOx (g) -A- K2SO4 (g) A K2SO4 (s)

Figure 33: Chemical equilibrium diagram for cooling of the flue gases (produced by combustion of the wood pellets based producer gas in an air fuel ratio of 1.1) from 1100-400oC for the S system

Temperature ( C)

-o- HCl (g) -P- KCl (g)

Figure 34: Chemical equilibrium diagram for cooling of the flue gases (produced by combustion of the wood pellet based producer gas in an air to fuel ration of 1.1) from 1100-400oC for the Cl- system

4.5 Conclusions and Recommendation

In the updraft gasification of biomass for application with GT, the carryover of alkali metal compounds in the gas phase is detrimental to the operation of the turbine unit. It is necessary to understand the formation of these compounds and to determine their quantity yield in an updraft gasifier using pellets fuels.

Product gas generated through updraft biomass gasification process yield less corroding compounds than other biomass combustion gases.

- Updraft gasification of wood pellets is possible, but tests with reed canary grass pellets are very problematic due to slagging problems related to ash melting.

- It is possible to obtain about 99% of the alkalis retention in an updraft gasifier from the parent loading in the raw fuel for wood pellets. But the 1% carried in the gas stream amounts to about 1200ppbw of the product gas, which is higher than recommended (i.e. 20ppbw) for direct firing of GT application.

- The concentration of Ca, Pb and V are within the acceptable limits for application of gasified wood pellets in GT applications.

- The formations of sulfates are preferential over the chlorides in the condensation reactions simulated in high temperature heat exchanger surface. The dominant deleterious alkalis formed in the high temperature heat exchanger emanate from K. Na concentration is too low to be detected in the gas phase in wood pellets gasification. The retained K- species in the ash are in the form of K2Ca (CO3)2 compounds.

- The Cl is converted to HCl when there is sufficient S to form K2SO4 instead of the KCl which condenses on heat transfer surfaces. HCl, when formed, are transported in the gas phase and passed out in the exhaust stream. This means that the risk of Cl induced corrosion in the heat exchanger surface would be lower than when utilizing other biomass based combustion gases.

- The combustion of product gas for wood pellets would contain very low quantities of K about half of that contained in the product gas stream. The use of two stage combustion

process for external gas turbine application would alleviate the problems of alkali metals compounds condensation and corrosion of turbine blades. • The study on alkali metal compounds condensation reactions of the process of product gas combustion serve as a qualitative indicator which requires verification through long term test with a high temperature heat exchanger; to study the corrosion and fouling with intention to obtain quantifiable performance data.

5. Downdraft Gasifier Product Gas Tar Content from Wood

Pellets and Wood Cylinders fuels

5.1 Introduction

Biomass fuels come in different sizes, shapes and densities, and the gasification technology is very fuel specific [74]. Normally wood residues are either available in a form that requires some method for size reduction or they are in the form requiring some process for densification. There is great need to balance fuel sizes to the gasifier design because with fine fuel there is risk of clogging the gasifier throat leading to shut down, and with larger fuel than required there is risk of having combustion reaction dominating the gasification process resulting into poor gas quality. Most biomass fuels used in the gasification technology from wood are in form of pellets, chips, cylinders and briquettes though some now use black liquor as well. Wood saw dusts can be turned into briquettes or pellets thereby increasing their densities and ease of handling. This would mean more energy per unit volume of the refined fuel and better operation of the gasifier.

In wood gasification tar is one ingredient in the producer gas whose generation depends on the fuel characteristics. Tar carryover in the gas stream and its subsequent condensation in gas handling units have undesirable consequences in IC engine applications and heat exchangers. The challenges of efficient tar separation from the producer gas have slowed the development of biomass gasification technology applications integration with IC engines. This is evident from the fact that different fuels have varying physical and chemical characteristics, which determine their tar yield quantities during the gasification process. The more tar yield the more cleaning is required and with it comes the economic penalties. Refer to section 2.4.1in chapter 1 for a detail discussion on tar issues in producer gas.

A study done on biomass gasification revealed there exist a conceptual relationship between the yield of tar and the reaction temperature [25], while others cited levels of tar yields for various reactors with updraft gasifiers at about 12 wt % of wood fuel and downdraft less than 1wt % of wood. These reports show that down draft gasifiers generate less tar than updraft gasifiers with a given biomass fuel. It is also known that downdraft gasifiers operated under atmospheric pressure are attractive for small scale applications (<1.5MWt) with IC engines and that there are potential markets for them in developing economies [75]. These advantages make them suitable for IC engine application compared to updraft or fluidized bed gasifiers.

A 20kWt atmospheric downdraft gasifier was chosen for studying the quantities of tar yield from wood cylinders and wood pellets gasification. The fuels are considered for possible application in biomass power plants in rural areas of Uganda. In this work wood pellets and wood cylinders were studied to determine their tar yield quantities when used as fuel in a down draft gasifier. The interest was to compare tar yields from wood pellets and wood cylinders with the intention of determining the differences, if any, in their tar yield when used as gasifier fuel anticipated for applications with IC engines. The goal of this study was to investigate the yields and to further determine the tar content and tar composition in the producer gas generated from the two fuels.

5.2 Experiment

5.2.1 Fuel

The fuels used in this case were pine wood cylinders of approximately 6 mm diameters cut to length of about 5-20mm and wood pellets formed from saw dusts of similar wood which has been compacted under pressure to 6mm diameter. The chemical composition and moisture content of the fuels were determined and values are shown in Table 18.

Table 18: Wood fuels analysis results

| Element | Wood Cylinders | Wood Pellets [wt. % of dry matter] |
| --- | --- | --- |
| Ca | 49.3 | 50.4 |
| Ha | 6.1 | 6.1 |
| Oa | 44.1 | 43.0 |
| Na | 0.1 | 0.1 |
| Sa | <0.01 | <0.01 |
| Asha | 0.2 | 0.4 |
| Moisturea | 7.4 | 7.0 |

4 Weight %

5.2.2 Experimental setup

The set up consisted of a simple down draft gasifier made of short stainless steel pipes of 150mm internal diameter joined together by bolts and nuts through flanges welded on the pipes. Details of the gasifier interior is shown in Figure 36

The gasifier, with setup shown in figure 35, had three air nozzles of 10mm internal diameter designed so as to cause a swirl flow across the combustion zone. The air nozzles were connected through a volume flow meter on the air inlet to the gasifier (Figure 36 section B-B). The gasifier was properly insulated to avoid heat loss through the wall. Three type-K thermocouples were connected to a computer through an analog-digital converter. A simple cyclone for gas cleaning was connected in line with two filters parked with pebbles for quick tar condensation. A three phase 0.5 kWe fan blower was used to draw air through the gasifier and this was installed after the filters with the outlet connected to a concentric tube combustor.

Test Equipment layout

A valve welded between the gasifier outlet and cyclone filter pipe-line provided a tar sampling point. The outlet from the valve was enclosed using a rubber septum to provide sealing for air leakages into the line during gas sampling. The reduction zone was initially filled with char of corresponding fuels under test

Figure 36 : Diagram Showing a Cut Section through the down draft and Section B-B showing the combustion zone details

5.2.3 Procedure

Combustion of the fuel at startup was enhanced using gun powder. The gasification processes yielded a combustible gas within one minute of ignition of the fuel. Identification of gas combustibility was achieved by flaring out through the simple concentric pipe combustor connected through the fan outlet. A butane torch was used as a pilot flame in the startup for gas flaring. The gas was considered combustible while the flame was self-sustaining. Four experiments were carried out on the two fuel samples with each sample having two separate tests lasting about 35 minutes each. Temperature values were recorded on the computer during the runs and the average for each fuel type was determined. A sampling probe allowed for Solid Phase Absorption (SPA) method for producer gas tar sampling p6]. Gas samples were drawn through a port welded on the gasifier gas output line. Figure 37 shows the sampling unit drawing. The opening and closing of the port was controlled by a 12.5 mm ball valve. Sampling line was kept at about 200°C using electrical heater to prevent tar condensation in the line.

1: to syringe 2: adapter 3: sample reservoir 4: Sorbent cartridge 5: fritted disc 6: amino-phase sorbent 7: septum 8: septum nut 9: "T" junction 10: hypodermic needle 11: heating tape.

Sampling commenced after the outlet gas temperature had reached about 230oC. This temperature was attained after about ten minutes of run because the gasifier was small and properly insulated and thereby reaching stable temperatures quickly.

Figure 37: Sampling unit [76]

Samples were drawn by passing 100mL of producer gas through a 500mg parked bed of amino propyl-bonded silica. The process took about one minute using a syringe plunger whereby tar vapours were trapped within the packed bed inside a small polypropylene cartridge. Five sealed sorbent cartridges from each run were sent to the Department of Chemistry laboratory of the Royal Institute of Technology in Stockholm Sweden for analysis.

5.3 Results

The gasifier rated at about 20kWt allowed for feedstock consumption rate of about 3.1kg/hr of wood cylinders with gas generation rate of about 6.2 Nm3/h resulting in Equivalence Ratio (ER) of 0.29. Consumption rate of wood pellets was about 2.94kg/h and with the resulting ER of 0.27 the gas generation rate was about 5.7 Nm3/h. Temperature readings were recorded for the combustion zone, reduction zone and at the gasifier gas outlet.

Figure 38: Combustion zone temperature with wood pellets and wood cylinders

Figure 39: Reduction zone temperature with wood pellets and wood cylinders

Figure 38 shows the plot for average temperature values in the combustion zone for the two fuel samples. Temperature values in the combustion zone recorded had averages of 1082oC and 870oC for wood pellets and cylinders, respectively. At the reduction zone, temperatures up to 780oC and 750oC with wood pellets and cylinders respectively were recorded. The average temperatures in the reduction zone for three experiments are presented in Figure 39. The gas output temperatures were about 230oC for both fuels.

13:00 13:02 13:04 13:06 13 :OS 13:10 13:12 13:14 13:16 13:13 13:20 13:2.2. 13:24 13:26 13:23 13:30 13:32

Real Time

900

O 	1	1	1	1	1	1	1	1	1	1	1	1	1	1	1	1	1	1	1	1

13:00 13:02 13:04 13 :OS 13:<XS 13:10 13:12 13:14 13:15 13:13 13:20 13:22 13:24 13:26 13:23 13:30 13:32 13:34

Real Time

5.4 Discussion

Results from tar analysis revealed that most of the tar constituents had molar masses below 300 and therefore of lower boiling point. Tar content in the producer gas stream was determined from results of analysis data of Table 19 with average values of about 3.45±0.85g/Nm3 and 2.03+0.23 g/Nm3 including margin of errors at 95% confidence level for wood pellets and cylinders, respectively.

A statistical test was made on the difference between the samples mean values using the student t-tests at the significant level of 0.05. The null hypothesis was that the two averages were equal and with the alternative hypothesis that they were not equal. A two tailed test result showed that the probability of occurrence of the null hypothesis was 0.018 which was less than the significance level of 0.05 so that the null hypothesis was rejected at 95% confidence level. There was a significance difference in the average tar quantities from the two fuels.

Wood pellets gasification process had higher combustion zone temperature than wood cylinders as shown in Figure 38. This meant that wood pellets produced more gas flux than wood cylinders in these tests. The finding is in agreement with other studies that have shown that it is more difficult to thermo-chemically convert wood cylinders than pellets in to gas at a given volume flux of primary air [77]. Also another practical test with a tractor operated using a downdraft gasifier at the Swedish Institute for Testing of Agricultural Machinery indicated that the gas produced from pellets had much higher tar content than the gas generated from wood chips p8].

Tar formation and carryover in the gas stream was more with wood pellets than cylinders of similar sizes as can be seen from Figure 40. When compared to values of 0.5-5g/Nm3 expected of a downdraft gasifier, the average values obtained in this experiment are within ranges observed in other downdraft gasifiers, but this would also be considered relatively higher for IC engine applications [41].

|  | 10.00 -¦ |
| --- | --- |
|  | 9.00 - |
|  | 8.00 - |
| (U | 7.00 - |
| ra |  |
| ia | 6.00 - |
| & |  |
| Q | 5.00 - |
| c |  |
| c | 4.00 - |
| (U |  |
| o | 3.00 - |
| <u |  |
| Q. |  |
|  | 2.00 - |
|  | 1.00 - |
|  | 0.00 - |

- Char from Cylinders

- Char from Pellets

J=C

Sulphur

Hydrogen

Nitrogen Constituent

Oxygen

Volatiles

Figure 40: Plot of ultimate analysis tests on wood char from wood cylinders and pellets

The relatively low temperatures in the reduction zone could be one of the possible causes of tar yield quantity realized with both fuels. Normally it would be expected that the temperature range is about 800-1000oC [25], but in this case the average values fell between 600-700oC for both fuel types as seen in Figure 39. It can be deduced from this finding that the low temperatures in the reduction zone allowed more tar to pass into the gas stream without being cracked.

Table 19: Average tar composition in g/Nm3 of gas

| Average quantities of tar constituents of producer gas |
| --- |
| Sample ID | Wood Pellets [10-2xg/Nm3] | Wood Cylinders [10-2xg/ Nm3] |
| Benzene | 81.01 | 33.62 |
| Toluene | 42.13 | 18.88 |
| p-Xylene | 12.37 | 9.39 |
| o-Xylene | 20.20 | 11.92 |
| Indan | 6.11 | 7.48 |
| Indene | 17.47 | 7.47 |
| Naphthalene | 19.10 | 7.50 |
| 2-Methylnaphthalene | 2.54 | 3.64 |
| 1-Methylnaphthalene | 0.00 | 0.00 |
| Biphenyl | 3.48 | 1.67 |
| Acenaphthylene | 7.21 | 5.24 |
| Acenaphthene | 2.28 | 4.37 |
| Fluorene | 7.65 | 7.34 |
| Phenanthrene | 8.61 | 7.58 |
| Anthracene | 6.09 | 2.68 |
| Fluoranthene | 11.80 | 11.99 |
| Pyrene | 12.27 | 6.12 |
| Phenol | 28.56 | 18.63 |
| o-Cresol | 12.23 | 7.99 |
| m-Cresol | 15.86 | 10.98 |
| p-Cresol | 9.81 | 5.95 |
| 2,4-Xylenol | 4.30 | 3.49 |
| 2,53,5-Xylenol | 9.02 | 5.36 |
| 2,6-Xylenol | 3.15 | 2.43 |
| 2,3-Xylenol | 1.24 | 0.95 |
| 3,4-Xylenol | 0.73 | 0.58 |
| Total average | 345.22 | 203.25 |

Samples taken from the char bed for each of the fuel type revealed, after analysis, that there was high retention of the volatiles in the wood cylinder char with values of 8.9% of dry matter compared to 4.4% for wood pellets (see Figure 40 for details). This remarkable difference could be attributed to the combustion characteristics of these two fuels which to some extent can also be traced to their physical structure differences. Studies have shown that different structures of fuel would have different combustion and gasification characteristics, which in turn affect the producer gas composition and quality p7]. Wood cylinders have low combustion efficiency compared to wood pellets of similar sizes of particular wood fuel. The results could then be used to interpret the relatively lower combustion temperature of the cylinders compared to pellets of similar sizes.

Slow pyrolysis process for the cylinders resulted into slow generation of volatiles which constituted mainly the producer gas, tar and water vapor. The retention of the volatiles with wood cylinders was higher in this case and therefore less volatiles in terms of tar and water vapor was realized out of wood cylinder gasification as compared to the pellets. And because nitrogen was used to extinguish the combustion process, its percentage in the dry matter increased by about 0.3 percent. Gasification process for pellets achieved more yields of volatiles due to the loose structure that allowed for easy heat transfer and volatiles vapor transfer within the body of the pellets. And the high porosity of the char created in the high temperature zone could not retain volatiles as would be possible with char from wood cylinders.

The quantities of tar from both fuel was significant, which can be attributed to low reduction zone temperature as noted earlier. Since this was a comparative study between the two fuel types subjected to similar treatment, the unfavorable gasifier behavior which is a function of its design and size was overlooked. The result of this study indicated, that it is possible to conclude that wood cylinders give less tar than pellets of similar sizes for a given biomass fuel.

5.5 Conclusions

The use of biomass from wood and agricultural residues is increasing with applications in thermal engines. Biomass fuel suitability for these applications depends on matching them to particular gasifier design for the desired application. The following conclusion can be drawn from this study:

- Tar realized from wood pellets and wood cylinders gasification process were constituted mainly of low molecular mass hydro-carbons of molecular mass less than 300.

- Wood pellets generate more tar than wood cylinders of similar physical dimensions. This is resulting from the combustion and reduction zone temperatures which are higher with wood pellets than with wood cylinders.

- Wood pellets provide good fuel for gasification processes suitable with thermal applications

- Wood cylinders, even chips, with obvious gas cleaning, are suitable for gasifier -IC engines applications.

6. Effects of Tar Sample Storage on Analysis Results

6.1 Introduction

The advantages of biomass as a sustainable fuel are almost being equaled by the challenges of transforming it into a competitive fuel for any purpose. The challenges are even deep routed in the stringent qualities that the consuming mediums require for effective and reliable operations and productivity. In the gasification of biomass for IC engines applications, gas quality consideration is paramount with respect to the energy content. The consideration is generic from the gasification process, which relates to ash-particulates, tar and alkali metal compounds. Down draft gasifiers are preferred to remedy tar problems in IC engines. These gasifiers are known to generate less tar, which is the most undesired and difficult constituent to eliminate in the gas stream intended for powering IC engines. Ash particles are eliminated by low cost filtration methods for producer gas cleaning (refer to section 2.5 for details).

Tar yields from biomass gasification process can be quantified and its constituents analyzed. This is done to understand their formation and to identify how to influence their formation. The process of tar sampling from producer gas has gone through some changes from the tedious 'Tar Protocol' method to the simplified online tar sampling and analytical techniques. One method under consideration now is the use of Solid Phase Absorption (SPA) technique with amino propyl-silane base as the absorbent medium ^ [25].

The simplification of tar analysis with SPA technique is suitable for samples that are not more than five hours away from the laboratory. Samples obtained from processes in remote locations which are many hours of drive from the laboratory may require some criterion for handling because of the expected degeneration of the samples. The level of deterioration that results from the samples delay (of over five hours) before analysis is not known and therefore the treatment to be accorded the results from delayed samples is also not known since there is no available literature on it.

In field work related activities, samples delay of up to five days are anticipated especially for those to be transported from Africa to Europe. This work assessed the level of deterioration that accrued from effects of tar samples stored for five days. Three groups of samples were each accorded different treatment; the first group was kept under room temperature of 20oC, the second group stored at -19oC and the third group analyzed within five hours from sampling as recommended for SPA method. The differences between the analysis results of the samples were determined.

The study was carried out to understand the level of deterioration so as to find ways of compensating for errors in results when delays are inevitable in analyzing samples. It was anticipated that some sort of relationship(s) could be developed to show the level of deteriorations and that possible correction factors could be arrived at which would allow for correction of analysis results of the delayed samples.

- Experimental Setup and procedure

Tar samples were taken during the experiment to determine the alkali metals retention in an updraft gasifier with wood pellets. Details of the setup and startup are discussed in chapter 3. After one hour of run when steady temperature readings were registered, 15 samples were drawn from the producer gas with each sample taken after every one minute. The samples were numbered 1 to 15 and then divided into three groups by picking them randomly using a random number table. The groups were treated in the following manner with X representing the sample number:

- Group G1X (Standard): Analysis was done within 5 hours from the sampling time

- Group G2X: Kept in the refrigerator at -19oC for five days and then analyzed on the sixth day.

- Group G3X: Kept under room temperature for five days and then was analyzed on the sixth day.

- Analysis Results and Discussion

The finding from the analysis in Table 20 shows details of the tar constituents' quantities in g/Nm3 of producer gas. The quantities of tar generated is shown plotted in Figure 41.

Sample number

Figure 41: Tar group sample quantities

According to the above tar analysis there are two groups of hydrocarbons realized i.e. aromatics and phenolics. Both groups had relatively lower boiling points below 260oC and therefore easily carried in the gas phase at producer gas temperature of about 300oC. The quantities of the constituents forming tar are presented in Table 20. A quick look at the results revealed that there were some differences between tars from the standard group (G1X) and the controlled groups (G2X and G3X). These differences are more pronounced in the phenolics compounds and they can be of significant implications in practical applications. Attempt has been made to quantify the

difference in this chapter. The accumulative effects of the individual hydro-carbon compounds

condensations have the consequence of increasing total tar load in the producer gas stream. Table 20 : Quantities of Tar constituents in x10-2g/Nm3 of Producer gas an updraft gasifier

| Constituents | Boiling Point OC | G1-1 | G1-2 | G1-3 | G1-4 | G1-5 | G2-1 | G2-2 | G2-3 | G2-4 | G2-5 | G3-1 | G3-2 | G3-3 | G3-4 | G3-5 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Benzene | 80.1 | 363.8 | 192.7 | 202.4 | 227.8 | 268.9 | 31.2 | 28.1 | 18.5 | 17.8 | 16.9 | 139.8 | 129.9 | 132.4 | 158.7 | 124.6 |
| Toluene | 110.6 | 75.4 | 65.6 | 67.8 | 74.0 | 84.1 | 41.8 | 26.8 | 13.4 | 14.3 | 15.4 | 56.0 | 53.6 | 52.8 | 56.3 | 49.2 |
| m/p-Xylene | 130 | 15.3 | 24.4 | 25.1 | 29.0 | 30.9 | 355.8 | 34.9 | 0.2 | 13.6 | 12.2 | 17.3 | 15.3 | 16.9 | 18.9 | 16.9 |
| Indane | 176.5 | 90.9 | 9.6 | 27.0 | 30.7 | 38.2 | 58.4 | 349.1 | 247.2 | 197.9 | 224.1 | 16.8 | 12.5 | 16.3 | 21.4 | 14.8 |
| Indene | 180 | 22.9 | 27.0 | 31.7 | 22.3 | 26.6 | 48.3 | 53.8 | 30.0 | 23.4 | 29.2 | 249.0 | 249.9 | 260.5 | 280.0 | 257.0 |
| Naphthalene | 218 | 161.2 | 323.5 | 330.0 | 340.2 | 385.5 | 12.8 | 42.7 | 38.5 | 31.9 | 29.6 | 81.3 | 84.5 | 87.8 | 96.8 | 86.1 |
| 2-Methyl- naphthalene | 241 | 62.3 | 116.6 | 119.4 | 130.3 | 146.2 | 28.9 | 12.8 | 13.6 | 11.3 | 10.8 | 33.4 | 33.1 | 32.9 | 33.5 | 31.6 |
| Ace- naphthene | 279 | 11.8 | 37.9 | 11.8 | 15.1 | 20.2 | 21.2 | 25.5 | 23.7 | 20.0 | 18.2 | 11.8 | 12.4 | 12.4 | 11.3 | 11.6 |
| Phenol | 181.7 | 95.7 | 13.6 | 38.8 | 46.0 | 50.1 | 19.9 | 18.2 | 16.1 | 13.6 | 12.5 | 19.9 | 20.4 | 20.6 | 19.9 | 19.3 |
| o-Cresol | 191.5 | 26.4 | 22.2 | 13.3 | 16.3 | 15.8 | 19.0 | 15.0 | 8.7 | 8.8 | 10.5 | 14.3 | 14.6 | 14.8 | 14.6 | 14.1 |
| m-Cresol | 202.8 | 8.0 | 17.2 | 23.3 | 27.4 | 28.0 | 3.2 | 21.2 | 16.5 | 13.2 | 16.4 | 12.2 | 12.5 | 13.5 | 14.7 | 12.4 |
| p-Cresol | 201.8 | 51.6 | 17.3 | 17.7 | 22.1 | 21.7 | 0 | 2.8 | 5.3 | 4.4 | 4.5 | 21.1 | 20.5 | 20.6 | 19.4 | 19.3 |
| 2,4-Xylenol | 211 | 5.8 | 25.7 | 17.5 | 20.8 | 21.4 | 0 | 0 | 2.5 | 2.1 | 1.9 | 5.7 | 6.0 | 6.2 | 6.5 | 0.0 |
| 2,5/3,5- Xylenol | 219 | 22.3 | 8.1 | 23.7 | 26.7 | 27.2 | 0 | 0 | 0 | 0 | 0 | 2.0 | 2.1 | 2.2 | 2.0 | 2.0 |
| 2,6-Xylenol | 203 | 12.1 | 2.3 | 8.4 | 2.8 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 2,3-Xylenol | 217 | 1.2 | 0 | 2.5 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 3,4-Xylenol | 227 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

A careful observation of Table 20 also shows that there was some dispersion of the higher hydrocarbon for the control samples. Indene species seem to increase in the case of storage at - 19oC, while naphthalene showed a decrease in quantity. Generally, the higher hydrocarbon seems to have an unexplained transformation, which could not be explained through this experimental work.

It was therefore important to understand the differences in the results obtained for the three different sample groups of which statistical approach proved handy. Firstly, the experimental data was analyzed for similarities among the three groups. Secondly, a simulation approach based on random number generation was used to generate more data for further statistical treatment and to enhance inference on the experimental data statistics. The standard deviation of the sample means for the groups were determined which allowed for development of hypotheses relating the different groups. The hypotheses tests were carried out on the sample-mean-differences between two groups to check for any similarity of data, and this allowed also for a substantial inference on the sample data parameters. Preliminary results of statistical treatment of experimental data are given in Table 21.

The difference between sample means were determined by using hypothesis tests with the student's t-test. With a significant level of 0.1, the hypotheses were developed and null hypotheses were rejected after testing and the results are presented in Table 22.

6.4 Statistical Treatment of Results

Table 21: Group statistics with quantities in mg/Nm3

|  | Group 1X | Group2X | Group 3X |
| --- | --- | --- | --- |
| Averages | 1.020 | 0.690 | 0.496 |
| Standard deviations | 0.103 | 0.038 | 0.129 |
| standard error | 0.046 | 0.168 | 0.058 |
| Error of margin at 95% CL | 3.06 | 1.12 | 3.86 |

The difference between two samples means method was used to determine similarity between the data for the different sample groups. Comparison between two samples meant that samples could both be within the acceptable range for IC engine applications, but showing significant statistical differences with implications in engineering applications, or they could have significant statistical differences but of no engineering significance. This would be expected when determining similarities between the samples that were accorded different treatments.

The statistical analysis presented in Table 22 revealed that the differences between the samples were significant. This meant that there were some kind of deteriorations which took place on the controlled samples, G2X and G3X. The cause(s) of the deteriorations could not be determined by this experiment, but it is known that some of the constituents making tar compounds can diffuse through plastic materials given time and suitable conditions p7], and to what extent this can contribute to the deterioration in sample quality is not known.

Table 22: Testing differences between sample means

| Variables |  | Values |  |
| --- | --- | --- | --- |
|  | G1X and G2X | G1X and G3X | G2X and G3X |
| Null Hypothesis | G1Xmean= G2Xmean | G1Xmean=G3Xmean | G2Xmean=G3Xmean |
| Alternate Hypothesis | G1X-mean^G2Xmean | G1Xmean^G3Xmean | G2Xmean^G3Xmean |
| Standard Error | 0.103 | 0.129 | 0.038 |
| Confidence Interval | 95% | 95% | 95% |
| Degree of Freedom | 8 | 8 | 8 |
| t-score | 7.097 | 6.755 | 3.223 |
| Probability of t-score | 0.00001 | 0.00001 | 0.00122 |
| Significance level | 0.1 | 0.1 | 0.1 |
| Result | Reject null hypothesis | Reject null hypothesis | Reject null hypothesis |

Note: G1Xmlan, G2Xmlan and G3XXmean are mean values for the different sample groups G1X, G2X and G3X respectively.

Tar quantity plots from the experimental results presented some difficulty in leading to a conclusion about the variations between the sample groups. The differences in variations realized in experimental work for particular sample groups could be attributed to the normal unsteady thermo-chemical reactions in the gasifier generating the producer gas. If reality was ideal, the reaction would be homogenous and steady, and then the plots in Figure 41 would have been horizontal lines, save for occurrences of random errors in analysis process that will cause some variations from linearity. The distances between the lines would be the same as that between their intercepts. Those differences between the intercepts of standard and controlled samples would then reflect the deviation of analysis results from the standard, after sample deteriorations, thus representing the error values for correction of results. Reality is random, and so is the plot in Figure 41, which required some statistical treatment of the results in order to determine the correction necessary for controlled samples.

Considering experimental data, the number of samples realized was very small. Considering the differences between average values, it can be inferred that for 5 days delay of samples kept at room temperature, analysis results required that a correction be effected by adding 524.2 Ig/Nm3 of tar content to the measured value. Similarly, for samples kept at -19oC for the same period of time would require addition of 330.0|g/Nm3 (see Table 23 below).

Table 23 : Correction Factors for Tar Storage

| Treatment | Experiment [¦lg/Nm] |
| --- | --- |
| 25°C | 524.2 |
| -19oC | 330.0 |

These corrections were based on calculations with results from wood pellets experiments. It therefore requires more detailed study before any conclusive correction factors can be arrived at. This also means that each fuel may have different levels of deterioration and call for tests to determine those levels before any storage method can be employed.

6.5 Conclusion and Recommendations

- Correction factors for tar samples collected using SPA method and analyzed after more than five hours are necessary in order to capture the true quantities of the constituents. It was possible from this work to see that the deterioration of tar samples when not analyzed within a certain time frame is evident.

- One particular area of interest is to obtain samples and store them under different environmental conditions for a finite number of days while analyzing some each day. In this way, it is possible to come up with some sort of deterioration correlations, which could yield non-linear plots. This could be gasifier and/or fuel specific plots.

- In this work, it has been shown that there is deterioration of samples during storage, like the dispersion of the higher molecular mass hydrocarbons. There is need to find out what could be the main reason for the deterioration, which through this experiment it was not possible to determine.

7. Field Study of a Biomass Gasifier IC Engine System

- Introduction

In order to understand challenges related to biomass gasifier IC engine systems, a study was conducted to determine causes of a reported deterioration in performance of an installed biomass power plant in Uganda. This unit was supplied by the Indian company Ankur Scientific Ltd. The plant is installed at a tea factory in Muzizi, in Kibaale district of Western Uganda, about 300km from Kampala, the capital city of Uganda. The plant was commissioned in the end of the year 2005. The commissioning was done in a period of about four weeks. Training of the staff in operating and servicing the plant was carried out during the commissioning period and this took ten days. The expected performance of 205 kWe gross power output (a 180kWe net output after deduction of auxiliary power) was not achieved during commissioning. The plant could generate about 180kWe gross without auxiliary loads.

Since commissioning, the performance of the power plant has deteriorated. The objective of this study was to identify possible reasons for this and suggest measures that would make it possible to reach the output originally achieved. At Makerere university there was an ongoing research in application of biomass for electricity power generation, in particular studies in improvement methods for biomass gasification power plants, in Uganda. With this research program there was a focus on capacity building in gasification technology expertise and the development of knowledge base and dissemination center for Uganda. The information about the reported deterioration in performance of the Muzizi biomass power plant provided an avenue for collaboration with the industry.

A study was carried out on the performance characteristics of the power plant, and an inquiry was made on operating experiences gained so far on the plant that had been installed at the factory. This information was vital in finding a solution to the deterioration in performance of the system as reported by the proprietors. It was also significant for the understanding of challenges related to the biomass gasification technology application for small scale electricity generation in Uganda in general. This chapter therefore describes the plant at Muzizi tea factory, its performance details, challenges and recommendations regarding ways to reinstate the plant to delivery its designed power output.

- Description of the installation

The power plant consists of a machine hall with the gasifier, gas treatment system, engine generator set and control panels, an adjacent building for fuel preparation and fuel storage and a combined spray pond and sludge pond where the scrubber water is cooled and contaminants in the water are allowed to settle at the bottom.

A flow scheme showing the main features of the installation in the machine hall is shown in Figure 42 below.

Figure 42: Flow scheme for the Muzizi power plant

The gasifier is of the downdraft type with a wet seal at the bottom. It is equipped with 8 air nozzles taking in air at a rate determined by the load on the engine. Air is drawn by a blower fan downstream the filters, augmented by the turbochargers suction pressure. Fuel is supplied batch wise through a lock hopper at the top of the gasifier after being carried to the gasifier top by an elevator. The fuel used is eucalyptus wood from the plantation managed by the tea estate which is cut into billets. The moisture content of the fuel used in the gasifier is checked at intervals by the factory engineer.

The producer gas generated in the gasifier passes a cyclone filter and closely thereafter a water scrubber. The gas then passes a series of bed filters; a coarse filter (CF) and two fine filters (FF1 and FF2), followed by a fabric filter, called safety filter (SF). The filtration system from CF to SF is built in parallel to allow filter service without much downtime.

So far the system is under slight vacuum and the flow is ensured by a blower that increases the pressure to slightly above atmospheric just before the flow control valves. After the blower, the gas passes a water trap and a valve battery that can be used to direct the gas either to a flare port, used during start-up, or to the engine in run-mode for power generation. When the generator is connected to the load, the gas flow is directed through a manually operated valve (V7) used for manual control of the fuel air mixture when loading and unloading the engine.

In the gas-air mixer, designed as a simple T-connection, the gas is mixed with air that is taken in from the hall through an air filter. The pressure at the mixer is a slight vacuum and the flow is ensured by the suction of the engine, enhanced by the two parallel compressors of the twin turbochargers. A part of the piping (BFR) is provided with a leather flap that is supposed to relieve pressure in case of back-flash from the engine. Throttle valves after the compressors are connected to a speed governor for automatic speed control during load variations.

The gas engine is a 12 cylinder spark ignition engine in V-arrangement, from Cummins India, with a displacement volume 28 liters and a compression pressure ratio at cranking of about 14.5. It is equipped with two Holset turbochargers, one for each side of the V block. The operating speed is 1500 rpm. The generator is from Newage Electrical India and is rated for 440 kVA at 415 V. The exhaust gas is brought to a recovery boiler for generation of steam to be used in the processing of the tea, but this is not being used.

A weighing scale is used for determination of the mass of fuel wood charged into the gasifier. Simple U-tube manometers are used to monitor the pressure differences over gasifier nozzles, across gasifier fuel bed and the different filters. A manometer is also used to measure the pressure after the blower. Pressure readings taken during this study were made using electronic pressure measuring equipment (Testo 512 with ranges of 0-200hPa and 0-2000 hPa). Temperatures of engine coolant and of the gas after the compressor are measured by temperature gauges installed on the engine. Engine operating hours and electrical power output are also measured. Sampling ports for gas analysis are available at the cyclone, the safety filter (SF) and on the engine intake manifolds.

Clear step-wise instructions are shown on large panels attached to the walls of the machine hall. All operating parameters are recorded each 30 minutes on standardized log-book sheets. No heat recovery is being used at the moment. The equipment appears to be in good working condition. By opening the flap of the back-fire relief section of the pipe leading to the turbocharger compressor inlet it was possible to inspect the inside of this pipe. No signs of tar or ash deposits were found.

7.3 Operational Experiences

The failure to reach the original target output of 205kWe has already been mentioned. It is not clear what the reasons are, but they are probably to be sought in the selection of the turbochargers or that compensation for the altitude was neglected. The accumulated operation time of the engine was 7435 hours at the time of this study. The plant was saving significant amounts of money by replacing power from the diesel electricity generators, when it was operated at loads over 150kWe.

It was noted that the power output of the plant dropped with time, originally from 180kWe to about 100kWe. When this level was reached, experts from the supplier were called in and found that the reason was poor gas heating value, caused by air leakage into the gasifier bottom. It turned out that the bottom had corroded as a result of high water level in the water seals, an effect of ash/char deposits in water lock space that had not been removed as part of the service routine. After repairs, the power output was brought up to about 150kWe, but again after a few weeks it dropped down to about 100kWe. New visits of experts from the supplier resulted in adjustment of the spark timing and in June 2007 again an improved output, this time, of 185kWe was achieved. After some months a gradual drop of the output was observed. In April 2008 the output had dropped to about 110kWe and operation was stopped since the engineer feared that continued operation, at that capacity, might lead to deposits in the engine. The operation was resumed in 2009 to date at loads not reaching 110kWe. Details of the earlier repair work by the suppliers were not divulged to the owners.

The experience from the operation of the scrubber system where scrubber water is brought to a spray pond for cooling and sedimentation of contaminants appears to be favorable in this plant. No liquid bleed-off is necessary since more water is evaporated by the sprays than condensed from the raw gas in the scrubber. The sludge collected in the pond is removed from time to time. How the sludge was handled thereafter is not discussed in this study and remains an important issue, since the sludge can be an environmental hazard.

7.4 Possible Reasons for the Degradation of the Output

- Low density of the fuel-air mixture entering the cylinder

Possible causes:

- Impaired turbocharger function (wear, deposits)

- Reduced pressure before turbo-charger (increased pressure loss in air filter)

- Stuck speed control valve

- Increased pressure loss over inlet valves (deposits)

- Poor heating value of the fuel-air mixture

Possible causes:

- Reduced heating value of the producer gas (air leakage into hot part of system, increased fuel moisture, bridging in the fuel bed)

- Deviation of air-fuel ratio obtained in the producer gas and air mixer from optimum (wrong valve settings on gas side, increased pressure loss across air filter, air leakage into cold parts of the system)

- Low conversion efficiency of the engine

Possible causes:

- Reduced compression ratio (valve leakage, leakage past piston rings)

- Failure to ignite in some cylinders (faulty spark plugs, faulty ignition system)

- Ignition timing deviates from maximum brake torque (MBT) position

- Increased back-pressure in exhaust pipe (deposition)

- Improper producer gas- air mixture ratio

7.5 Evaluation of the fuel gas preparation process

In bid to determine any short fall in the performance of the fuel gas preparation process, tests were carried out on wood moisture content, wood fuel consumption, char quantity yield, gasifier wall temperature, gasifier air intake quantity, pressure drop in the producer gas cleaning filters and product gas composition. The findings are presented in the following sections.

7.5.1 Wood moisture content

Wood fuel from eucalyptus logs of 0.5m length are split and are left to dry in stacks under the open sky. The split logs are then cut into billets of about 8x10x6 cm dimensions. The billets are further dried under a roof which shields it from rain. There are variations in the sizes with some small and others large creating fuel wood of non-uniform moisture content for the different fuel sizes. Samples of wood fuel were collected and weighed, and later dried at 110oC in an oven for 24 hours after which they were weighed again. Table 24 shows the results of tests carried out on 10 samples giving average moisture content of the fuel wood at 17.7% on a dry basis, which is equal to 15.0 % on wet basis. This is within the specifications provided by the supplier, which is between 5 and 20% moisture on wet basis.

Table 24: Results of moisture content for Muzizi Plant

| Moisture content analysis |
| --- |
| Sample | Wet weight[g] | Dry weight[g] | Moisture [%] |
| 1,0 | 169,2 | 142,3 | 18,84 |
| 2,0 | 225,9 | 190,9 | 18,33 |
| 3,0 | 158,7 | 134,0 | 18,49 |
| 4,0 | 227,2 | 198,4 | 14,54 |
| 5,0 | 134,8 | 113,7 | 18,53 |
| 6,0 | 250,9 | 211,6 | 18,54 |
| 7,0 | 117,8 | 101,1 | 16,50 |
| 8,0 | 327,8 | 277,4 | 18,15 |
| 9,0 | 152,0 | 128,9 | 17,93 |
| 10,0 | 238,7 | 203,6 | 17,26 |

7.5.2 Wood consumption

The specific wood consumption claimed by the supplier is 1.2 to 1.4 kg/kWh at full load. Using the log-book records for the months of June 2007, July 2007, March 2008, November 2009 and March 2010 the specific wood consumption recorded by the operators can be used to calculate the specific fuel consumption at different loads. The results are shown in Figure 44. Also included are results from measurements during site visits. The data for June 2007 were recorded immediately after the power output was restored by experts from the supplier of the plant and at 1.1 kg/kWh actually indicates better performance than claimed. The reduced efficiency at lower loads indicated by the data lower outputs can be expected, because some energy losses in the gasifier are more or less independent of the load and since the efficiency of the engine will drop with load. For an output of about 100kWe the log book data and the measurements are in good agreement. At loads around 50kWe, the log book records indicate much larger specific fuel consumption than the measured data. As illustrated in Figure 43, the log book data for 11 days in

March 2010 show large variations. The reasons for this are unknown, but it is possible that the records are not always reliable.

As shown in section 7.5.3, a mass balance made on basis of the measurements for a generator output of 46 kW indicate that the measured feeding rate at 50 kW is reasonably accurate.

Figure 43: Specific fuel consumption determined from logbook data and measured on two site visits.

Figure 44: Power output and specific wood consumption in the Muzizi power plant in year 2009 and 2010 7.5.3 Gasifier performance

The studies of gasifier performance could only be made for an output of 46 kW, since it was not possible to find more electrical load.

Gas sampling after the safety filter was carried out by making use of the blower pressure to fill

the sampling bags through the pressure measurement nipples. The gas composition measured is shown in Table 25 below.

Table 25: Gas composition after the safety filter (volume fractions in dry gas)

| H2 | N2 | CO | CH4 | CO2 | LHV MJ/Nm3 |
| --- | --- | --- | --- | --- | --- |
| 19,51% | 49,77% | 14,88% | 1,56% | 14,28% | 4,71 |
| 16,31% | 53,78% | 17,11% | 1,43% | 11,38% | 4,60 |
| 17,60% | 48,41% | 20,97% | 1,06% | 11,97% | 5,11 |
| 17,49% | 48,64% | 18,34% | 0,92% | 14,61% | 4,70 |
| 16,03% | 51,08% | 20,64% | 1,20% | 11,04% | 4,94 |
| Average 17,39% | 50,34% | 18,39% | 1,23% | 12,66% | 4,81 |

These samples were taken at different times while the plant was under normal operation. The values are not varying much with the exception of some percentage of oxygen in the gas which probably came as a result of leakage in the gas handling system during sampling and/or analysis. The gas compositions reported in Table 25 have been adjusted to 0% oxygen in the gas. The LHV presented were determined by using the average composition calculated in the Equation 5 obtained from the work of Reed and Das [28]:

LHVgas=11.2 [H2] + 13.1[CO]+37.1[CH4]+83.8[CnHm]	[Equation 5]

The range of heating values is exceeding the specifications of the supplier, i.e. between 4.2 and 4.6 MJ/Nm3.

The dry gas volume flow can be calculated from the air volume flow to the gasifier from a mass balance for nitrogen given in Equation 6 below:

T> iT ' 0.79

Vg - Vair—	[Equation 6]

a	VN 2

The air flow into the gasifier was determined by measurements of the velocities at the air inlets with a digital air flow meter (Testo 435) using hot wire anemometer probe. The gasifier had eight equally spaced air nozzles around the combustion zone supplying air into the zone. With the air flow meter placed across each of the nozzles, average air flow velocities through all the nozzles into the gasifier were determined. Measurements were carried out at the same time gas samples were being taken. Four different values were recorded within two hours for all eight nozzles with the average values presented in Table 26.

The average air flow velocity determined from the above measurements was about 4.18 m/s and 3.70 m/s for plant with flaring of the gas and operating with generator load of 46 kW, respectively. The total nozzles cross-sectional area was determined to be 0.0157 m2. This corresponded to an average air flow rate of about 209.2m3/h into the gasifier through the nozzles when the engine was running. With atmospheric pressure 0.87 bar and the air temperature 27oC, this is equal to 0.046 Nm3/s. For a nitrogen volume fraction in the gas equal to 50.34% according to Table 25, the dry gas flow will be 0.072 Nm3/s.

Table 26: Air flow velocity through nozzles of 50mm diameter

Average airflow

|  | Engine off, flaring | Engine Running |
| --- | --- | --- |
| Nozzle | m/s | m3/h | m/s | m3/h |
| 1 | 4.85 | 34 | 3.75 | 27 |
| 2 | 4.01 | 28 | 3.58 | 25 |
| 3 | 3.31 | 23 | 3.33 | 24 |
| 4 | 4.84 | 34 | 4.59 | 32 |
| 5 | 4.84 | 34 | 3.3 | 23 |
| 6 | 4.42 | 31 | 3.32 | 23 |
| 7 | 3.87 | 27 | 3.68 | 26 |
| 8 | 3.31 | 23 | 4.04 | 29 |
| Average | 4.18 | 236.4 | 3.70 | 209.2 |

Figure 45: Three photographs showing combustion process as viewed through the nozzle hole

K*

The amount of char extracted each hour was determined to be about 27kg/hr with the sizes as can be seen in Figure 46.

Figure 46: Char samples from Muzizi power plant

The scrubber water temperature was about 31oC with values recorded after two hours of run. This means that the amount of water vapor in the gas after the scrubber can be estimated to about 4.4 %.

From the gas flow and the heating value of the gas, the energy conversion efficiency of the generator set can be calculated as shown in section 7.5.5.

Visual inspection of the of the air nozzle holes during gasifier run showed red hot char being consumed in the gasification process as can be seen in Figure 45 and meaning the process was functioning well.

kg/h

A mass balance for the gasifier at a generator output is shown in Table 25.

Table 25: Gasifier mass balance at 46 kWs

e

% of feed

Wood, in Air, in Dry gas, out Water vapour ,out Char, out

150 211

41,5 58,5 80,3 14,0 7,5

290

51

27

-6

-1,8

Deficit, inflow - outflow

The dry gas flow was calculated from a nitrogen balance and the flow of water vapor in the gas from a hydrogen balance. The mass balance shows a deficit of 1.8% which must be considered as acceptable accuracy.

The temperature of the gas leaving the gasifier could not be measured. According to the specifications presented by the supplier, this shall be in the range 400-500oC. A measurement of the temperature around the grate area of the gasifier at the outside was made with an IR thermometer, which gave 330oC.

No corrosion was seen around the ash pot on the outside of the gasifier. 7.5.4 Pressure drop across the gas filters

The gasifier unit generates the raw producer gas, which carries with it some tar as well as ash and char dusts. Cleaning of the gas is effected by water scrubbing and filtration through beds of coarse and fine wood particles and finally through a fabric safety filter. In this process unsanctioned leakage of the air into the gasifier could result into complete combustion of the wood fuel inside the gasifier subsequently generating a gas of very low heating value. Leakage into the gas cleaning system can dilute the product gas, thereby lowering the energy content per unit volume. All these situations can result in a drop in the power output of the gas engine. There is a fundamental difference between air leakages in the hot side and the cold side of the system. Air leakage into hot gas may lead to combustion of H2 and perhaps CO and therefore a reduced heating value of the gas. Air leakage into cold gas can, at least for small leakages, be compensated for by changing the gas-air ratio through the mixer. The result of such air leakages is however a dangerous situation. If the mixture ignites before engine entry, a serious internal explosion may result. The sizes of the water lock at the bottom of the gasifier flap of the back- flash relief may not be large enough to avert a major destruction of the filter section.

Pressure drops measured along the filters during gasifier operation with the gas being flared and with engine running with a generator load of 46 kWe are shown in the Table 26.

Table 26: Pressure drop across the gas filters

Operating status Flaring Load Design operating

46 kW	range

|  |  |  | Min | Max |
| --- | --- | --- | --- | --- |
| CF | 49.0 | 9.8 | 49.0 | 490.3 |
| FF1 | 294.2 | 245.2 | 294.2 | 784.5 |
| FF2 | 49.0 | 49.0 | 294.2 | 784.5 |
| SF | 29.4 | 29.4 | 29.4 | 392.3 |

The observed values are well within the specified ranges, except for the CF where lower pressure drop than expected was noticed. This could be an indication that the filtering process in the CF was not performing as required yielding more filter load into the fine filters. Otherwise the conclusion is that high pressure losses in the gas treatment part of the plant cannot explain the deterioration of the output.

7.5.5 Conversion efficiencies

At 15% moisture (wet basis), the LHV of wood is about 15.9 MJ/kg. With a wood consumption of 1.1 kg/kWh at 150 kWe generator output recorded in June 2007, the overall electric efficiency will be 21%. The measurements made at a generator output of 46 kWe gives an overall electric efficiency of 7.6%

The cold gas efficiency of the gasifier could only be determined at a generator load of 46 kW. With the gas flow of 0.072Nm3/h and LHV for the gas of 4.81 MJ/Nm3 as reported in section 7.5.3 the cold gas efficiency is 56.8%. An energy balance for the gasifier at this generator load is shown in Table 27.

Table 27: Gasifier energy balance at 46kWe

kW	%

Fuel energy 664.0	100

Chemical energy in gas 347.0	52.3

Sensible energy in gas 50.0	7.5

Energy lost with char 215.6	32.5

Heat loss to surroundings 51.4	7.7

The energy balance is based on an assumed gas temperature of 400oC which could be reasonable for the low end of the operating range. As shown by the energy balance, the energy lost with charcoal leaving the gasifier dominate the losses and account for 32.5% of the fuel energy input at this gasifier output (about 35kWe). If this loss and the heat losses to the surroundings are assumed independent of the load and the gas temperature at the outlet at full load (185kWe) is assumed to be 500oC, the cold gas efficiency at full load can be estimated as 71 %. This is slightly better than the efficiency claimed by the supplier, which is 69.4%. It can be concluded that the gasifier operates close to specifications and that the reason for the deteriorated output must be sought in the engine.

From the measurements of gas flow and gas heating value the efficiency of the generator set i.e.

fuel gas to electric efficiency can be calculated as 13.2% at a generator load of 46 kW. This is much lower than the efficiencies claimed by the supplier for full load (29.4%9 and 50% load (24.5%). The load during the test was only 22% of the rated output 205 kWe and a low efficiency should be expected. An increase of the brake specific fuel consumption for spark ignition engines by 50% when the load is reduced to about 20% is not unreasonable. In this case it appears that the brake specific fuel consumption has increased by a factor of 2.2 which indicates that something is wrong.

7.6 Tests on the gas engine

The engine is equipped with two turbochargers, each one connected to one of the intake manifolds of the V-block .The turbochargers each drew air-fuel mixture from the same source and they enhanced fuel mixing before intake into the cylinders. The following parameters required assessments on the engine, namely; engine compression ratio and turbocharger boost.

7.6.1 Check on compression ratio for the IC engine

As mentioned before the IC engine was a V12 engine utilizing spark plugs for ignition. The compression tester used had a small graph card and plotter which traces the pressure build- up in the cylinder from first compression to the firing stroke. This test was to determine the cylinder pressures at cranking of the engine, which meant the distributor cap was removed in this case.

In the testing process, one power spark plug was unscrewed, at a time, and a pressure gauge was connected to its recess through a tube designed to engage into the spark plug recess on the cylinder head. The tube used had a rubber end plunged into the recess that contained a special valve which can allow one way pressure build up into the gauge. The whole unit shown in Figure 47 is held down by hand in place.

Figure 47: Compression machine operation

In order to record the compression pressure for a cylinder the unit was held in place such that there was no pressure leak from the spark plug threaded recess. The engine was cranked until there was no more increase in the pressure noted. The pressure from the cylinder under test was directed into the pressure gauge. The values were plotted on the graph card marked in bars. Each stroke of compression accumulated more pressure until the exhaust stroke when the exhaust valve of that cylinder was open. At that point the plotter recorded the maximum pressure buildup and remained locked until the pressure was released by squeezing the spring loaded nonreturn valve for the next recording to be taken.

The values of pressures recorded for all the cylinders are shown in Figure 48 with very little variations among the cylinder pressures tested by cranking the engine.

14,7

14 13,9 13,8

1 2 3 45 67 89 10 11 12 Cylinder No.

Figure 48: Compression Test Results

The engine is equipped with two turbo chargers of unknown performance data. On one of the turbo chargers, the name plate revealed the model as a 4LGK. Pressure readings taken from the engine while in operation is presented in the table 28.

Under normal circumstances the pressure generated by the turbo charger compressor must be able to give a boost that would create a pressure ratio well above 1.4 for improved engine power output delivery. Pressure readings before the turbo chargers were below atmospheric, at about 0.23kPa under. The pressure could not be measured directly after the turbo charger compressor, only after the speed control valve where it was found to be 3.74kPa below atmospheric pressure at the load of 46 kW. This is a possible condition at part load, but disconnecting the valve control from the computer and attempts to increase the engine speed by manual change of the valve position had no effect. This indicates that either the valve is stuck or that the turbochargers are not running.

Figure 49 shows a scheme for the turbo charger unit and the pressure measuring points used in this study.

Figure 49: Turbo charger unit scheme and gas flow

Table 28: Pressure readings from Muzizi power plant gas engine.

Gas flow throw the turbo charger

| Location | Readings [hPa] | Average [hPa] | Engine speed [RPM] | Load [kW] |
| --- | --- | --- | --- | --- |
| Before compressor , 1 | -2.2,-2.3,-2.4,-2.3,-2.3,-2.4 | -2.3 | 750 | 0 |
| After speed control valve, 2 | -21, -22, -19,-22,-20 | -20.8 | 750 | 0 |
| Exhaust after turbine ,3 | 148,143,145,143 | 145 | 750 | 0 |
| Before compressor,1 | -4.3,-4.2,-4.2 | -4.2 | 1500 | 46 |
| After speed control valve, 2 | -37,2,-36.9,-38.3,-37.6,-37 | -37.4 | 1500 | 46 |
| Exhaust after turbine, 3 | 344,341,342,343 | 342.5 | 1500 | 46 |
| Before safety filter, see Figure 42 | 53.9,54,53.8,53.7 | 54 | 1500 | 46 |
| After manual control valve, V7, before gas/air mixer, Figure. 42 | 43.1,42.2,43.2, 43.2 | 43.2 | 1500 | 46 |

Note: 1hPa =0.1kPa

The temperature of the gas-air mixture in the inlet manifold at 46 kW load was measured as 35oC.

7.6.2 Exhaust gas analysis

The analysis of the exhaust gases revealed that there were some variations in the engine combustion performance. As shown in Figure 50, the CO content in the exhaust emission was low with average value recorded of 0.25%, and that of O2 was at about 2.5%. These values would vary a lot under normal operation depending on the loading and amount of air in the system.

Figure 50: Muzizi exhaust emission 1900-2000hrs

These quantities show operation on lean fuel with an equivalence ratio of 0.82. The drastic changes of the oxygen content recorded in some of the tests could be attributed to engine load response behavior, which sometimes led to engine stop. Load response characteristics of the engine were not quite understood and the operators thought that this could be the effect of the improper setting of the engine fuel feed control module. It is obvious that operating the engine at an equivalence ratio closer to 1.0 would allow more power output. The heating values of mixtures at equivalence ratios of 0.82 and 1.0 will be 2.20 and 2.44 MJ/Nm3 respectively. Increasing the equivalence ratio to 1.0 could therefore improve the output by about 11%. This is apparently not sufficient for reaching the rated power output.

The exhaust gas temperature was read from a temperature meter mounted on the exhaust pipe which read values of 320oC and this value was verified by the infra-red thermometer, which meant normal combustion was taking place as expected in a typical IC engine.

7.7 Discussion

The observations that have been made indicate clearly that the reason for the deteriorated output must be sought downstream of the air-gas mixer, i.e. in the engine or the exhaust channel. The engine appears to be operated with a lean mixture, but this alone cannot explain the loss in performance.

The pressure after the speed control valve is low, but this alone cannot explain the low maximum output. Based on the product gas flow and the exhaust gas analysis, the volumetric efficiency of the engine can be estimated to 0.64. A normal value would be in the range 0.85 to 0.9. This means that for operation at equivalence ratio 1.0 and with a more reasonable volumetric efficiency, the power output could be increased by at least 47%. Adding the effect of turbocharging with a charging pressure ratio of 2, would give an increased power output of at least a factor of 2.4 to 2.5 from the 46 kWe run during the test. This would give an output of about 115 kWe. Possible simple explanation for the deterioration from this capacity is either that the speed control valve are stuck (which is indicated by the experiences reported in section 7.6.1) or that the turbochargers have failed. The lack of charging pressure at the low load is however to be expected and this explanation is therefore less credible.

A further improvement of the output would be possible if the pressure losses in the exhaust channel could be reduced. The pumping power required at the tested load of 46 kW for an inlet pressure of -3,7 kPa (gauge) and a pressure in the exhaust pipe of +34.3 kPa (gauge) will be about 13 kW. The pressure losses in the exhaust system will increase roughly proportionally to the square of the exhaust flow and this pressure loss will certainly be limiting the output. Records for the development of the pressure in the exhaust pipe are not available, but it is possible that soot accumulation in the recovery boiler have caused an increasing pressure in the exhaust system. The low volumetric efficiency can partly be caused by a high pressure in the exhaust pipe leading to more residual gas in the cylinder.

7.8 Conclusions and Recommendations

- The power plant made it possible to save significantly on fuel costs when it performed as in the early period of operation. The deterioration of the performance after a relatively short time will however discourage others from switching from diesel generator sets to wood gasifiers and IC-engines. For promotion of biomass based, small scale power generation in Uganda, it is important that the reasons for the loss of capacity are clarified, so that measure to maintain the rated output can be taken.

- The reasons for the loss in capacity must be sought in the engine or the exhaust system downstream. The gas quality is within specifications or better and the pressure losses in the gas treatment system is within specifications.

- The engine appears to be operated with a lean fuel mixture, but adjusting that alone will not improve the power output significantly.

- It seems that the main reasons for the impaired output are low pressure in the inlet manifold, low volumetric efficiency and high pressure losses in the exhaust pipe.

- It is recommended that the speed control valves, the turbo chargers are dismantled for inspection and if necessary renovated and also that the recovery boiler is inspected and if necessary cleaned. Also the timing of the firing must be checked and adjusted if necessary. New tests where the plant can be loaded to its maximum capacity shall then be carried out, with measurements similar to those reported here.

- It is important that the experiences from the power plant are documented and disseminated to other interested parties. When operation of the Muzizi plant has been resumed careful monitoring of the operating experiences and operational parameters are to be made.

- Finally it is recommended that tar samples from the gas at the cyclone and at the safety filter (at least three samples at each position), a sample of the liquid in the cooling pond and a sample of the sludge found in the bottom of the pond be taken for analysis. Analysis of these samples will indicate if additional steps, in treatment process, should be taken in order to avoid negative environmental impacts.

8. Biomass Gasification Investment Opportunity for Small

Scale Applications in Uganda

8.1 Introduction

Most developing countries are putting a lot of funds to importation of petroleum fuels to meet their energy demand, which electricity power generation and transport sectors are the major consumers. In Uganda an estimated US$500 million (UGsh820 billion) worth of petroleum was imported in 2004, which represented about 23.5% of the national budget in the financial year (2004/2005) [79]. The increasing numbers of automobiles, population and industrial growth rates of 30%, 3.8 and 5.8% per annum, respectively (2008 estimate) [2] [80], suggests a comparative increase in consumption of petroleum products. Both production and transportation are greatly dependent on imported fuel whose base price is controlled by foreign countries and the implication is that changes in world oil prices have direct impact on the local market prices of goods and services. One author noted that one reason most countries end up in debts is when their petroleum fuels import grows to 10% of the total national import [80], which can be the case for Uganda.

It is possible that domestic prices for petroleum products may drop in the future when Ugandan oil is introduced into the market. Unfortunately this speculation is difficult to ascertain due to inadequate information on Uganda oil production projections. Diesel fuel greatly used by industries in their standalone electricity power generation units and in heavy trucks currently costs about US$ 1.0/L (An exchange rate of Uganda shillings to United States Dollars (US$) giving US$1.0 equivalent to 2000Ugsh has been used in this paper), but carries a subsidy to allow US$ 0.725/L for electricity power generation plants with capacity above 200 kWe. With the expected increase in World market prices for petroleum products, it is unforeseeable that the diesel price per liter can be halved by introduction of Uganda fuel into the local market.

In Table 29, the current electricity tariff in Uganda is presented and compared to that from United States of America [81] (USA). The pinch of the electricity price in Uganda can be understood by the great disparity between Gross Domestic Product (GDP) at Purchasing Power Parity (PPP) per capita of the two countries where US $ 1300 and US $ 47900 are reported for Uganda and USA respectively: The figures attest the fact that a unit price of electricity in Uganda is more expensive than in USA. The situation in Uganda is that electricity coverage is only about 5% [82]of the total population compared to 100%, 100% and 98% for USA, Sweden and Egypt, respectively [3] as an example.

Initially electricity power came mainly from one hydro-power station of about 380 MW which was not producing enough power to meet the demand due to its limited capacity. Thermal electricity power generating units were installed to abate the electricity power deficit that climaxed in 2006 due to prolonged drought that caused a tremendous drop in water levels of Lake Victoria [83] and to meet the increasing demand. The thermal units come with inherent costs from imported petroleum fuels of which costs are transferred to the consumers inform of high tariffs.

Table 29 : Uganda electricity tariff by consumer category

|  |  | Uganda | USA |
| --- | --- | --- | --- |
| Consumer Type | Tariff Particulars ( kWh) | Cost US$/(kWh) | Cost (US$/kWh) |
| Domestic | <15 >15 | 0.031 0.214 | 0.1155 |
| Small and Medium Scale Industry | Average | 0.200 | 0.1025 |
| Large Scale | Average | 0.094 | 0.0696 |

Currently construction of a new hydro power generation station (Bujjagali on River Nile) is ongoing and it is expected to produce about 280 MWe when commissioned in 2012. There is anticipation that it will present some opportunity for a reduction in electricity power tariff to the consumers and provide also reliable supply as well. It is also known that electricity power connections is not about to reach the vast rural settlements in Uganda and some of the isolated production industries in remote areas. Areas which are still deemed uneconomical to connect to the national electricity grid lines would be forced to use thermal power plants in form of petroleum fuel guzzlers or renewable energy resources powered systems.

This study compared the investment options between biomass gasification-gas engine and a diesel engine generator sets in Uganda. Particular interest was directed in determine the initial investments and rates of return on investments for the two systems.

8.2 Biomass Fuels - Availability Issues

There are lucrative business opportunities in meeting the energy deficit in some areas through exploitation of the locally available biomass resources in Uganda. Gasification is one of the biomass fuel transformation technologies for applications in conventional IC engines and GT applications. IC engines are more attractive than gas turbines in rural areas due to the simplicity of equipment and availability of local knowledge for service and maintenance requirements. Biomass gasification integrated with IC engines for 100kWe generations is economically favorable than steam turbine based systems with boilers [60].

Introduction of new methods and technologies is always met with suspicion and rejection at the extreme and at times this occurs for justifiable reasons [84]. In this particular situation there are challenges related to biomass fuel utilization for electricity power generation which amount from economic, social, political and environmental spectrum, and that gasification technology is not yet fully developed, adds to the odd. These challenges present the uncertainty of the anticipated benefits when such projects are undertaken. However such concerns can be addressed through information seeking and in consultations with recognized promoting institutions and other projects using similar technology.

Investment into biomass gasifier-engine system would require some sensitization and training for the entrepreneurs into understanding logistics planning and operational issues requirement related to the success of such undertaking. It is known that biomass gasification technology integrated with IC engines are economically viable, but like any other investment project, prior establishment of the biomass resources sustainability anticipated for application is obligatory for

future prosperity.

Due to the largely available biomass resources around the country such as in the urban areas, at the sugar mills and other sources like coffee industries. This study offers a quick insight into economic potential of biomass gasification technology integration with IC engines in Uganda. A study model of 100kWe generator is chosen in this case. The comparison between these systems based on wood fuel and a diesel generator set of similar output was carried out and discussed in this chapter. Biomass gasification process was presented in section 2.2 of this work. Table 30 shows the heating values of the fuel gas that can be realized when gasification is carried out with the oxidizing agent as either air, or with air and steam mixture. A rich fuel can be obtained by using the air-steam mixture with LHV of up to 11MJ/kg, but the costs in equipment investment and operation can be heavy for small units. It is also noteworthy that the LHV of 4.5MJ/kg is sufficient for IC engine application. It can be boosted by installation of a turbo charger on the engine for more power delivery from the engine. Therefore, air is the predominantly used oxidizer in the gasification process because it is availability at no cost.

Table 30: The variation of heating value with different oxidizers for biomass fuel

| v | Producer gas |
| --- | --- |
| Oxidizer | Lower Heating Value ( MJ/kg) |
| Air | 4.5-5.0 |
| Air/steam | 11.0 |

The power output from a modified 444kWt diesel rated engine (model: TB232, make Greaves) tested with producer gas from biomass gasification process gave a power output of 203 kW [85]. This can allow comparison on size difference between biomass and diesel system, for instance, the LHV for diesel fuel is about 43.4 MJ/kg and for air gasification process producer gas from biomass fuel is 4.5M J/kg, which explains the difference in sizes between biomass and the diesel powered systems. This difference in producer gas and diesel fuel energy contents is the main reason diesel systems are smaller than producer gas driven engine of comparable power output and is reflected in the price per unit power output for each one of them.

8.3 Biomass Gasifier and Diesel systems

Biomass gasification system integrated with an internal combustion engine is comprised of five units. These are the; gasifier gas cleaning units, internal combustion engine, generator set, and fuel preparation units. Depending on the gasifier size, it is important that suitable fuel sizes be used to allow a matching of the fuel physical characteristics to the gasifier for better performance. In that way bridging and holing can be avoided. Holing is the occurrence of a burnt-out of fuel in the middle of the gasifier creating a hole with more air intake through the gasifier than required for gasification process. Fine particles biomass fuels also develop high pressure drops in gasifier unit. All these phenomena affect the performance of the gasifier adversely with the consequence of poor gas quality. The result is that total system efficiency is reduced tremendously which is not desirable for any investment projects.

The gasifier type chosen for this study was a co-current (downdraft) gasifier. A wood gasifier

denoted as (WBG100) from Ankur Scientific [29] with effective thermal power output and gas flow rate of about 302 kWt and 250 Nm3/h, respectively. This was matched with an internal combustion engine connected to a generator of 100kWe power output. The gasifier was designed to run on wood billets with average dry fuel consumption of about 100 kg/h.

A comparative diesel generator set of 100kWe was also selected for this study with a fuel consumption of 28L/h.

8.4 Economics of Biomass and Diesel Systems

The chosen biomass system had a cost price of US$ 2087/kW [86] [87], which comprised of the entire gasifier unit, gas cleaning trains, IC engine and all auxiliary equipment for fuel preparation and handling, shelter construction and equipment installations costs. Operational and maintenance costs were estimated at 5% of the initial investment capital cost per year. Fuel cost was estimated at US$30/ton (metric) [86]. A typical fuel consumption of wood with 20% moisture content is estimated at about 1.36kg/kWht [17], and this is equivalent to US$30/MWht.

The diesel generator set was estimated at US$500/kW electric output [85]. Costs related to operation and maintenance was estimated at about 3% of the capital investment per year. The generator running at full load consumes 28L/h at a subsidized fuel cost of about US 0.73/L which constitutes US$203/MWht, but the price on unsubsidized diesel fuel is currently about US$280/MWht. In all these figures the exchange rate of Uganda shillings (UGsH) to United States Dollars (US$) was about US$1.0 to 2000UGsh.

An approximate unit price for electricity consumed of US $0.15/kWh was used in this analysis in order to project the income from the investments. This value is lower than the current electricity unit price for small and medium scale industries in Uganda (see to Table 29). One and two shifts operation times of 8 hours per shift were studied. These times relate to plant capacity power (PCF) of 33% and 66.7% respectively and correlate with the running times of most industries in Uganda.

Plots for electricity production costs and internal rate of return (IRR) against PCF are presented in Figure 51 to 53. A conservative value of 7% Capital Recovery Factor (CRF) was assumed for both systems. In Figure 51 electricity production cost for diesel system with subsidized fuel at US$215.9/MWhe is higher than that for biomass system of US$84.03/MWhe when compared at PCF of 33.3%. The situation is not different at 66.7% PCF with power production costs of US$57/MWhe and US$209/MWhe for biomass and diesel systems respectively. Biomass gasification process presents a payback period (PBP) of 4.6 years for PCF of 66.7% throughout the project life at IRR of 17% with a projected positive net present value (NPV). At 33.3% PCF the biomass plant showed IRR of -2% with a negative NPV, which projects no return on investment. The inflection points on the IRR curve is a result of the gradient change due to the none-linear scaling of the abscissa.

The situation with unsubsidized diesel is presented in Figure 52 showing also the IRR for diesel system as negative for all the PCF. In Figure 53, with a heavily subsidized diesel fuel, electricity production cost is lower with the diesel system for PCF less than 20%, but there is no return on investment as a negative IRR (-8%) for both systems are projected. With a heavily subsidized diesel fuel, increase in PCF presents a proportional rise in IRR for diesel system which gives more return compared to biomass system at the corresponding PCF. Diesel system projected losses for the investment in all cases represented with negative IRR.

Figure 51: Electricity costs estimates at different PCF with biomass and subsidized diesel prize 0.203 $/kWh

Figure 52: Electricity Costs Estimates at different PCF with biomass and unsubsidized diesel price of 0.28 $/kWh

An increase in PCF from 33.3% to 66.7% for biomass system presented a decrease in the unit costs of electricity production by about 32% and resulting to a PBP of 4.6 years. The worst case scenario for biomass system competing with a diesel system occurs at a diesel cost of 0.363$/L (US$ 0.1015/kWh), biomass system is competitive up to about 30% PCF above which diesel

system is performing better. Considering fuel costs at half the subsidized value this can result into diesel system coming up with PBP of 2.1 and 3.9 years at 33.3% and 66.7% PCF, while biomass system remains in the ranges of 4.8 and 10.9 years respectively. For the diesel cost to achieve these performances, which are conservative speculated figures for the future, Uganda should possibly be owning an oil refinery.

Figure 53: Electricity costs estimates at different PCF with biomass and a subsidized diesel price US$ 0.1015/kWh

(a)	(b)

Figure 54: Costs percentage contribution for (a) diesel system with fuel cost at US$0.280/kWh and (b) biomass system with fuel cost at US$0.03/kWh.

The costs contribution from all cost centers is presented in Figure 54 a and b. Fuel took the highest share of costs for diesel system and depreciation for biomass system. For biomass system capital cost in terms of depreciation is projected at about 60% of the total cost and by fuel at 36%. With diesel system 95.6% of the total cost is related to fuel and only 4% to depreciation. O&M took on lower percentage of the total costs for both biomass and diesel systems at 4.2%

and 0.3%, respectively. These values were determined for diesel at subsidized price of US$ 0.208/MWh.

A similar study done for Cambodia [88] had 73%, 16% and 11% cost representing depreciation, O&M and fuel respectively for biomass system. Diesel system had costs distribution of 67%, 24% and 9% for fuel, depreciation and O&M respectively. Diesel fuel is the predominant cost in this case as well, but the cost price is lower than in Uganda at US$ 0.18/kWh. Biomass fuel cost estimate was US$ 30/kWh. In that study biomass system investment had better returns on investment at PCF above 13%.

Diesel fuel prices are the main reason for the unfavorable economic returns from running the diesel system. What is happening with the industries currently operating the diesel system is that the costs incurred by the diesel system is covered by better returns (profit) in another part of the industry, which covers for the diesel deficit. In this way the diesel system seems to be a means to an end.

When biomass residues from waste streams are to be used then the cost likely taken by fuel is greatly reduced. Wastes such as bagasse, MSW and coffee husks (some authors refer to them as fuel at negative costs) can be utilized within the existing premises for those with operating industries producing wastes. This can increase the profitability of the investment of any kind incorporating biomass system to itself for application with wastes generated in-house.

8.5 Issues with Biomass Gasification Technology Systems in Uganda

There are numerous advantages biomass systems can afford in relation to energy production, environmental friendliness and in waste treatment. Gasifiers are very fuel specific and thus particular fuels require matching gasifier design to the available fuel type. The vast sources of fuel represent the diverse designs the gasifier units require under normal circumstances. This in itself makes the system not flexible enough unless other methods are used to prepare the fuels such as creating briquettes from fine powder, or carryout fuel size reduction through cutting or crushing according to desired needs. Only after such fuel transformation can the gasifier perform to expectation with various fuels. The fuel preparation equipment means additional capital costs for the investment.

The development of biomass gasification systems for application with internal combustion engines is not yet mature and there are technical challenges being experienced with currently installed systems especially procured from Indian manufacturers [86] [89]. It can be mentioned that the load response characteristics of current biomass systems available does not permit sudden loading after some part loading has been achieved. This therefore requires that the loads be gradually applied to avoid stalling of the engines. Load control mechanisms are available at additional costs to investments. The mentioned problem of loading is particular to certain industrial processes were intermittent runs under heavy loading are common.

Gas quality is among the significant issues in the biomass gasification process. Tars and dust particles are the main contaminants for the internal combustion engines, which their removal from the producer gas is vital. The filters usually get clogged in many circumstances resulting into less gas flow into the engine and subsequent output power reduction. Another related problem can arise from high moisture content fuels which also affect adversely the biomass system performance, and recommendations is that moisture content of raw biomass fuels be kept below 18% for better power output from the biomass system.

Resistance to change and acceptance of new technology by the operators are some other problems as well. Possible reasons arise when biomass systems are run in parallel and/or with diesel system as emergency plant unit. Issues related to the convenience of running diesel engine and to some extend theft of diesel fuel may cause some operators to sabotage the biomass system. Some of these issues were noted during field visits by the authors of this report and as long as there is diesel nobody would like to run the biomass system.

There is still great dependence on the suppliers for maintenance related issues. It can be partly that the suppliers create the void to allow some kind of market control with the equipment by offering inadequate training and information related to their equipment. At times it is just the owners who are sometimes concerned that their technicians cannot handle the maintenance work, especially when there is some serious breakdown. This has caused some gasifier systems to be shut down.

8.6 Conclusions

- Great potential avail itself for biomass gasification systems application with internal combustion engines in Uganda. This is achievable through the utilization of available biomass resources generated from agro-based industries by-products and planned plantations and MSW. Biomass systems stand competitive with diesel systems for electricity power generation with biomass systems presenting better investment returns.

- Fuel prices contribute greatly to the production costs of power from thermal electricity generator plants and in this particular study biomass have strong prospects for investment returns than diesel system due to greatly the cheaper fuel (US$0.03/MW) compared to (US$0.28/MWh). The competitiveness of biomass is even emphasized when biomass from waste streams are considered, and at relatively higher Plant Capacity Factor improved return on investment is realized within 4 years. This also leaves the equipment with a lot of life for more returns.

- Biomass gasification equipment can be locally made and it would greatly reduce on the costs of equipment. Additionally there are subsidies that can be accorded through government intervention as part payment on the capital equipment investment costs or tax waiver. Other supporting institutional bodies advocating for clean energy can offer similar support as government would which are directed towards encouraging renewable energy system application for better environment. Any subsidy to biomass system lower power production cost per unit with the consequence of better returns and competitiveness against other power sources.

9. Future work

Biomass gasification is a feasible approach in meeting some of the energy needs in developing countries. Uganda has a great opportunity in embracing this technology to its prosperity. There are challenges as noted in this study and with these some recommendations have been made in every chapter. It would be good practice to close this report with emphasis on those recommendations which are to guide future work.

It was noted that EFGT system offers great advantage over directly fired GT systems. Its limitation comes in the form of low maximum operating temperature that the heat exchanger material can permit, which is something that require more research into materials engineering to solve thus out of scope of this work. Nevertheless, the current materials that would take a maximum operating temperature of 850oC would be sufficient and the major concern is the fouling, and possible deposition and corrosion in the heat exchanger unit. That part of the study should follow this work, to devise ways of averting deposition of corrosive entities in the heat exchanger units. Therefore a study in deposition o high temperature heat exchanger surfaces should be carried out.

There is need to determine the economic analysis of the EFGT system for application in Uganda. This would be compared to performance of a gas engine and diesel engine of similar capacity. Such determination of economic performances may reveal some unknown potentials and offer credible platform for decision making on the biomass gasification technology method to employ.

In this report also tar related challenges stands out strongly, and there are some simple methods that can be used to effect acceptable gas quality for application in IC engines as pointed out in this study. These methods fit the operating requirements in developing countries when less automation is favorable and equipment maintenance personnel technical knowledge is not very demanding. The use of biomass bed filters and fabric filters remains a feasible approach but require some standardization in design and cleaning medium to employ for the Uganda scenario.

There are various fuels from the agricultural residues and MSW whose tar content require determination. Knowledge of possible tar yield from these anticipated fuels for gasification would permit better decision on how to handle the gas cleaning process for the possible different capacities of the plants anticipated. This study should carry forward similar tests made in chapter 5 of this report on agricultural residues and MSW.

The inclusion of water scrubbers in gas cleaning would necessitate determining the content of the waste stream from a pilot project and to suggest ways on how the extracted waste can be treated.

There are problems experienced with imported technologies when proper training in operation and maintenance are not carried out. Through this study it has been identified as one problem affecting installed power plants in Uganda and in India as well from where some of these gasification equipment are imported. The construction of the equipment for biomass gasification is not a complex task especially where designs have been determined for a particular need. It is therefore interesting to study the requirement for such a venture of designing and fabricating gasifier units and auxiliary equipment locally. With this there would be a survey on potential market for such equipment through some kind of interviews with identified organizations. This should be able to present a definitive view of what level of contribution in the energy sector gasification technology can attain given introduction and time in Uganda.

Biomass can be a grand substitute to fossil fuel, especially in small capacity power plants in the rural villages of Uganda, but there is great need for a functional demonstration plant and establishment of a knowledge dissemination center.

References

- Uganda Government, Annual Report. Kampala: Ministry of Energy and Mineral Development, 2007.

- US Energy Agency. (2008, March) Photius.com. [Online]. htt://www.probonostats.wordpress.com

- United Nations Development Program. (2009, March) Geographic website. [Online]. http://www.photius.com/rankings/electrification by country 2007 2008.html

- City Council of Kampala. (2001) City Council of Kampala Website. [Online]. http://www.kcc.og.ug

- Bingh L P, "Opportunities for utilizing waste biomass for energy in Uganda," Oslo, 2004.

- Turyahikayo G R, Hatanga E S, Otti T, and Kegirungi P, "Renewable energy technologies dissemination in Uganda- The case of small hydro power plants," Kampala, 1996.

- Krani P K, Sustainable management of tropical rain forests in Uganda. Ontario: Common Wealth Secretariat, 1994.

- Forestry Research. (2008) Biomass Energy Centre Website. [Online]. http://www.biomassenergycentre.org.uk

- United States Department of Energy, "Opportunities for small biomass power systems," 2000.

- Yan J, "Externally fired gas turbien - Technical report," Stockholm, 1998.

- Rambush N E, Modern Gasifiers. London: Benn, 1923.

- Wikipedia. (2010, April) Wikipedia Encyclopedia. [Online]. http://en.wikipedia.org/wiki/1980s_oil_glut

- Michael A l J Jr. et al., "High yield biomass charcoal," Energy and Fuels, vol. 10, no. 3, 1996.

- Loewe O Jr, Black J R, Ross I J, and Payne F, "Economic potential for on farm biomass gasification for corn drying," 80-3508, 1980.

- Cruz I E, "Producer gas from agricultural waste," Resource Recovery and Conservation, vol. 2, no. 3, 1977.

- Peiy J, "The application of paddy husk gas in rice mill - In proceedings of the FAO/FHI Regional technical consultation on Agricultura waste fro farm energy needs," Suzhou, China, XF8333069, 1983.

- Maschio G, Koufopanos C, and Lucchesi A, "Pyrolysis a promising route for biomass utilization," Bioresource Technology, vol. 42, no. 3, 1992.

- Food and Agricultural organization of the United Nations, Wood gas as engine fuel:. FAO, 1986.

- Mckendry P, "Energy production from biomass (part 3): gasification technologies," Bioresource Technology, vol. 83, no. 1, 2003.

- Kirubakaran V et al., "Review on gasification of biomass," Renewable and Sustainable Energy Reviews, vol. 13, 2009.

- Elvin L Ip H, Scott J, Foster P, Mark Vickers, and Baxter Larry L, "Effects of schape and size on devolatization of biomass particles," Fuels, vol. 89, 2010.

- Lijun W, Weller Curtis L, David D Jonnes, and Milford A. Hanna, "Contemporary issues in thermal gasfication of biomass and its application to electricity and fuel productuion," Biomass andBioenergy, vol. 32, no. 7, 2008.

- Thermal Gasification of Biomass Task. , "EC and USDOE Meeting on Tar Measurement Protocol," Brussels, 1988.

- Elliott D C, "Relation of reaction time and temperatue to chmical comosition of pyrolysis oils," Denver, CO, 13:9780841215368, 1988.

- Baker E.G, Brown M.D, Elliott D.C, and Mudge L.K, "Characterization and treatment of tars from biomass gasifiers," Denver, CO, 1988.

- LaHaye P G and Zabolotny E, "Externally fired combine cycle of (EFCC).," Chicago, IL, 1989.

- Milne T.A, Evans R.J, and Abatzoglou N, "Biomass gasifier tars: Their nature, formation, destruction, and tolerance limits in energy conversion devices," Canada, 1997b.

- Reed T A and Das A, Handbook of biomass downdraft gasfier engine system. Golden, Colorado: Solar Energy Research Institute, 1988.

- Ankur Scientific Energy Technologies Pvt Ltd. (2008) Ankur Scientific Energy Technologies. [Online]. http://ankurscientific.com

- Sutton D, Kelleher B, and J R.H.Ross, "Review of literature on catalysts for biomass gasification," Fuel Processing Technology, vol. 73, no. 3, 2001.

- Xu C C, Donald J, Byambajav E, and Ohtsuka Y, "Recent advances in catalysts for hot- gas removal of tar and ammonia from biomass gasification fuel," Fuel, vol. 89, no. 8, 2010.

- Henriksen U et al., "The design, construction adn operation of a 75 kW two-stage gasifier," Energy, vol. 31, no. 10-11, 2006.

- Babu S P, "Thermal gasification of biomass- Workshop No.1: Perspectives on biomass gasification, Task 33," Chicago, 2006.

- Boerrigter H, Snader V.P, Patrick Bergman, and Rob Emmen Jan-Villem K, "Tar removal from biomass product gas, develpment and optimization of the OLGA tar removal technology," Paris, 2005.

- Zwart R W et al., "Oil-based gas washing - Flexible tar removal for high efficient production of clean heat and power as well as sustainalbe fuels and chemicals," Environmental Progress and Sustainalbe Energy, vol. 28, no. 3, 2009.

- Patel J, "Skive BGGE/CHP-IEA Task 33 Meeting," Chicago, 2006.

- Teislev B, "Haboore-wood chips gasifier and 1500 kW gas engines operating at 32% power efficiency in CHP configuration," Amsterdan, The Netherlands, 2002.

- Kirjavainen M, Siplia K, T Savola, Salomon M, and K Alakangas. (2003) Aboutus Organization Website. [Online]. www.http://habmi gern2003.info/PDF/Pyrolysis.pdf

- Nielsen P H, Frandsen F J, Dam-Johansen K, and Baxter L L, "Implications of chlorine associated corrosion on the operation of biomss fired boilers.," Progress in Energy and Combustion Science, vol. 26, 2000.

- Keller A, Kovacs R, and Homann K H, "Large molecules, radicals, ions, and small soot particles in fuel rich hydrocarbons: Part IV, Large polycyclic aromatic hydrocarbons and their radicals in a fuel rich benzene-oxygen flame," Phys Chem, Chem Phys, vol. 2, no. 8, 2000.

- Milne T.A, Evans R.J, and Abotzoglou N, "Biomass gasfiers "tars": Their nature, formation and conversion," Springfield, VA, NREL/TP-570 25357, 1998.

- Pritchad D, "Biomass combustion gas turbine," London, 2003.

- Traverso A, Magistri L, Scarpellini R, and Massardo A, "Demonstration of an exteranally fired micro gas turbine," Energy Resource Technology, vol. 12, 2003.

- Blander M, "TThe inorganic chemistry of the combustion of aspen wood with added sulfur," Biomass andBioenergy, vol. 12, no. 4, 1997.

- Quaak P, Knoef H, and Hubert S, Energy fom biomass- a review of combustion and gasification technologies. Washington D.C.: World Bank, 1999.

- Hasler P and Nussbaumer Th, "Gas Cleaning for IC engine applications from fixed bed biomass gasification," Journal of Biomass and Bioenergy, vol. 16, 1999.

- Nelson C E, "LM2500 gas turbine modification for biomass fuel opoeration," Biomass and Bioenergy, vol. 15, 1998.

- Brown M D, Baker E G, and Mudge L K, "Environmental design considerations for thermochemical biomass energy," Biomass, vol. 11, 1986.

- Salman H, "Evaluation of a cyclone gasifier design to be used for biomass fuelled gas turbine - Doctoral Thesis," Lulea, 2001.

- Traverso A, Massadro A, Aristide F, and Scarpellini R, "Externally fied micro gas turbine: Modelling and experimental performance," 2006.

- Graham R.G and Bain R, "Biomass gasification: Hot-gas cleanup. International Energy Agency, Biomass gasification working group," 1993.

- Ferrira S.B and Pilidis P, "Comparison of externally fired and internal combustion gas turbine using biomass fuel," Energy Resource Technology, vol. 123, no. 4, 2001.

- Taborek J, Heat exchanger handbook. London: Hemisphere Publishing Corporation, 1986.

- Duwig C, "Numerical and experimental validation of a gas turbine combustor design for gasified biomass combustion," Stockholm, 2000.

- Larson E.D and Williams R. H., "Biomass fired steam injected gas turbine cogeneration for sugar can industry. Proceedings of Research in Thermochemical Boimass Conversion," London, 1988.

- Mueller A C, Heat exchangers. Handbook of heat transfer. New York: McGraw-Hill, 1973.

- Frank O, "Simplified design procedures for tubular exchangers I. Practical aspects of heat transfer," Chem. Eng. Prog. Tech. Manual (Am. Inst. Chem.Eng.), 1978.

- Gupta J P, Fundamentals of heat exchanger and pressure vessel technology. New York: Hemisphere Publishing Corp, 1986.

- Cho S M, "Uncertainty analysis of heat exchanger hydraulic designs," Heat Transfer Engineering, vol. 8, 1987.

- Metropli N and Ulam S, "The Monte Carlo Method," Journal of American Statistical Association, vol. 44, no. 247, 1949.

- Kjellstrom B, "Research and development in application for micro-CHP from biofuels - Summary of activities in some European countries," Stockholm, 2007.

- Knudsen J N, Jensen P A, and Dam-Johansen K., "Transformation and release to the gas phase of Cl, K and S during combustion of annual biomass," Energy Fuels, vol. 18, no. 5, 2004.

- Kautz M and Hansen U, "The externally fired gas turbine (EFGT-Cycle) for decentralized use of biomass," Applied Energy, vol. 84, 2007.

- Di Blasi C, Signorelli G, and Protoricco G, "Counter-current fixed bed gasification of biomass at laboratory scale," Ind. Eng. Chem. Res., vol. 38, 1999.

- Gabra Muhammed, Arms Nordin, Marcus Ohman, and Bjorn Kjellstrom, "Alkali retention/separation during bagasse gasifcation: A comparison between fluidized bed and a cyclone gasifier," Biomass and Bioenergy, vol. 15, 2001.

- DIFRACplus, "TOPAS 2.1," Karlsruhe, 2003.

- Fredriksson C, "Exploratory experimental and theoretical study of cyclone gasification of wood - PhD Thesis," Lulea, 1999.

- Turns S, Kinoshita C, Ishmera D, and Zhou J, "The fate of inorganic constituents of biomass in fluid bed gasification," Fuel, vol. 77, 1988.

- Gilbe C et al., "Slagging characteristics during residential combustion of biomass pellets," Energy and Fuels., vol. 22, 2008.

- Kurkela E, Stahlberg P, Simell P, and Leppalathi J, "Updraft gasification of peat and biomass," Biomass, vol. 19, 1989.

- Zevenhoven-onderwater M, R Backman, Skrifvars B J, and Hup M, "The ash chemistry in fluidised bed gasification of biomass fuels. Part I: Predicting the chemistry of meltin g of ash and ash bed material interaction," Fuel., vol. 26, 2001.

- Bale C W and Pelton A D, "FACT-Win Version 3.05," Montreal, 1999.

- Bale C W et al., "Factsage thermochemical software and database," Calpha, vol. 26., 2002.

- Rajvanshi A.K, "Biomass gasification," in Alternative energy in agriculture, Yogi Goswani, Ed. India: CRC Press, 1986.

- Knoef H A M T, "Status and development of fixed bed gasification," Utrecht, Report EWAB 9929, 2000.

- Brage C, Yu Q, Chen G, and Sjostrom K, "Use of amino based absorbent for biomass tar sampling and separation," Fuel, vol. 17, 1997.

- R.C.E Friberg, "A new method to analyze the thermochemical conversion of solid fuels," Stockholm, 2000.

- Nordstrom O, "Account of research and testing activities in the producer gas field," Uppsala, 1963.

- Uganda Government, "The Uganda Budget 2004/2005 Citizen Guide," Kampala, 2005.

- Miguel Barrientos. (2008, January) Index Mundi. [Online]. http:www.indexmundi.com

- AMulya K N R, Williams H R, and Johansson B. T, "Energy After Rio: Prospects and Challenges," New York, 10 9211267013, 1997.

- Energy Information Administration. (2011, April) U.S Energy Information Administration. [Online]. http://www.eia.gov/

- Uganda Government, "Electrification rate," Kampala, 2005.

- Reibeeki H. (2006, March) Earth Observatory. [Online]. http://earthobervatory.nasa.gov

- Dana M, "Technology and market information for the next millennium.," Cashiers, North Carolina, 1998.

- Dasappa S. (2006, February) Combustion Gasification and Propulsion Laboratory Website. [Online]. http://www.cgpl.iisc.ernet.in

- Buchholz T and Volk T, "Designing short rotational coppices based bio-energy system for rural communities in E. Africa," Kampala., 2007.

- World Bank, "Technical assessment of off-grid, mini-grid and grid electrification technologies," ESMAP Technical Papers 121/07, 2007.

- Hitofumi A et al., "Potential for rural electrification based on biomass gasfication in Cambodia," Biomass and Energy, vol. 31, 2007.

- National Informatics Centre, Bangalore. Biomass Energy for Rural India. [Online]. http://bioenergyindia.kar.nic.in

- FAO, "Quarterly Bulletin of Statistics," FAO, United Nations, vol. 5, no. 4, 1992.

- Brage C, Yu Q, Chen G, and Sjorstrom K, "Tar evolution profiles obtained from gasification of biomass and coal," Biomass and Bioenergy, vol. 18, 2000.

- Bridgewater A V, "The technical and economic feasibility of biomass gasfication for power generation," Fuels, vol. 7, 1995.